## Table of Contents
Strategy II: Reference Case assumptions on demand, technology costs, TTCs, and RE targets. Higher RE bounds (with additional investments for RE integration). Build small hydro plants. Build a 60 MW biomass plant. Consume 100% of Sankofa production. High case natural gas development
| Contents |  | Each of the tabs in the file has the following run-year information for all Ghana (sum of model zones: North-GH, Southwest-GH, Southeast-GH, and Ashanti-GH)
0 | RefCase | Row# | 4 | 1. Reserve Margin Capacity Annual [MW] | Total annual reserve margin capacity in Ghana, as of January 1 of the specific run year
1 | High Demand | Row# | 5 | Plus Firm Contract Purchases Annual [MW] | Firm contract purchases of capacity from outside Ghana (none at present)
2 | Low Demand | Row# | 6 | Plus Transmission In Annual [MW] | Transmission connections that could supply peak MW to Ghana (in theory)--this includes the dummy plants in CIE and Burkina Faso
3 | HighFuelPrice | Row# | 7 | Less Firm Contract Sales Annual [MW] | Firm contract sales of capacity outside of Ghana (none at present)
4 | LowFuelPrice | Row# | 8 | Less Transmission Out Annual [MW] | Transmission of peak MW to countries outside Ghana--this include transmission of MW to CIE, CEB and Burkina Faso/Mali
5 | Limited Fuel Supply | Row# | 9 | Total Reserve Margin Capacity Annual [MW] | Addition/Subtraction of Rows: 4+5+6-7-8
6 | Greater Fuel Supply | Row# | 11 | 2. Peak Load Annual [MW] | Peak load in Ghana
7 | Limited Water | Row# | 12 | Less DSM [MW] | MW of peak demand savings from demand side management (DSM) programs that shave off peak load in Ghana
8 | HighRECapCost | Row# | 15 | Net Demand Annual [MW] | Addition/Subtraction of Rows: 11-12
9 | LowRECapCost | Row# | 17 | 3. Reserve Margin Annual [%] | Reserve margin for Ghana (considering net exports) in % : Row9/Row15 -1
10 | HighDemandHighCostLowWater | Row# | 19 | 3a.Local Reserves Annual [%] | Reserve margin in total% : Row4/Row15
11 | LowDemandHighCostLowWater | Row# | 21 | 4. Total Generation [GWh] | Total generation in Ghana
12 | LowREHighCost | Row# | 22 | Inter-Region Transmission [GWh] | Net Transmission (GWh transmission in - GWh transmisson out)
13 | LowConCapCost | Row# | 23 | Pumping & Storage Losses [GWh] | Losses of GWh due to pumping and storage (not relevant for Ghana)
|  | Row# | 24 | Plus Purchases [GWh] | Contractual purchases of GWh for Ghana (not relevant)
|  | Row# | 25 | Less Sales [GWh] | Contractual sales of GWh for Ghana (not relevant)
|  | Row# | 27 | 5. Total Supply for Demand [GWh] | Addition/Subtraction of Rows (Row 21+22-23+24-25)
|  | Row# | 29 | 6. Projected Demand [GWh] | Total Demand in Ghana
|  | Row# | 30 | Energy Not Served [GWh] | Unserved Energy (if any)
|  | Row# | 31 | Less DSM [GWh] | GWh of savings from demand side management programs
|  | Row# | 32 | Energy Demand Response [GWh] | GWh of savings from demand response programs
|  | Row# | 33 | Net Demand [GWh] | Addition/Subtraction of Rows (Row 29-30-31-32)
|  | Row# | 35 | 7. Dumped Energy [GWh] | Tiny amount of energy difference between Total Supply and Net Demand (Row 27-33) -- As long as this is small, there is no issue
|  | Row# | 37 | 8. Total Generation [GWh] | Total generation in Ghana, Same as Row 21
|  | Row# | 38 | Less T&D Losses [GWh] | T&D losses -- set to zero in GH-IPM v1.2018 version
|  | Row# | 40 | 9. Total Sales [GWh] | Addition/Subtraction of Rows (Row 37-38)
|  | Row# | 42 | 10. Capacity by Capacity Reporting Type [MW] | Block of Rows showing total net dependable capacity that is available for generation (Potential build rows shows what is actually built in the model for this scenario)
|  | Row# | 43 | 01 Potential Build Oil/Gas Combined Cycle | Capacity of potential builds of new combined cycle plants
|  | Row# | 44 | 01 Oil/Gas Combined Cycle | Capacity of existing and underconstruction combined cycle plants
|  | Row# | 45 | 02 Potential Build Biogas | Capacity of potential builds of new biogas plants
|  | Row# | 46 | 02 Gas Combustion Turbine | Capacity of existing gas-based combustion turbine plants
|  | Row# | 47 | 02 MSW - Landfill Gas | Capacity of existing landfill/MSW plants
|  | Row# | 48 | 02 Oil Combustion | Capacity of existing oil-based combustion turbine plants
|  | Row# | 49 | 02 Potential Build Oil/Gas Combustion | Capacity of potential builds of oil/gas-based combustion plants (combustion turbines)
|  | Row# | 50 | 02 Oil/Gas Combustion | Capacity of existing oil or gas-based combustion turbine plants
|  | Row# | 51 | 03 Hydro | Capacity of existing Hydropower plants
|  | Row# | 52 | 03 Potential Build Hydro Small | Capacity of potential Hydropower plants
|  | Row# | 53 | 04 Potential Build Nuclear | Capacity of potential nuclear power plants
|  | Row# | 54 | 05 Potential Build Interruptible | Capacity of potential interruptible power plants (these hypothetical plants are used to bridge gap in each of the model regions between demand and supply, including transmission, for that region)
|  | Row# | 55 | 06 Potential Build Solar PV | Capacity of potential Solar PV power plants
|  | Row# | 56 | 06 Solar PV | Capacity of existing Solar PV power plants
|  | Row# | 57 | 06 Potential Build Solar PV with storage | Capacity of potential Solar PV with battery storage power plants
|  | Row# | 58 | 07 Potential Build Biomass Combustion | Capacity of potential biomass combustion power plants
|  | Row# | 59 | 07 Potential Build Coal | Capacity of potential coal power plants
|  | Row# | 60 | 08 Potential Build Wind | Capacity of potential wind power plants
|  | Row# | 61 | Total | Sum of rows 43 to 60
|  | Row# | 64 | 11. Capacity Additions and Changes by Capacity Reporting Type [MW] | Block of Rows showing additions/changes in net dependable capacity that is available for generation (Potential build rows shows the changes of new build capacity, as is actually built in the model for this scenario)
|  | Row# | 65 | 01 Potential Build Oil/Gas Combined Cycle | Changes/Additions in capacity of potential builds of new combined cycle plants
|  | Row# | 66 | 01 Oil/Gas Combined Cycle | Changes/Additions in capacity of existing and underconstruction combined cycle plants
|  | Row# | 67 | 02 Potential Build Biogas | Changes/Additions in capacity of potential builds of new biogas plants
|  | Row# | 68 | 02 Gas Combustion Turbine | Changes/Additions in capacity of existing gas-based combustion turbine plants
|  | Row# | 69 | 02 MSW - Landfill Gas | Changes/Additions in capacity of existing landfill/MSW plants
|  | Row# | 70 | 02 Oil Combustion | Changes/Additions in capacity of existing oil-based combustion turbine plants
|  | Row# | 71 | 02 Potential Build Oil/Gas Combustion | Changes/Additions in capacity of potential builds of oil/gas-based combustion plants (combustion turbines)
|  | Row# | 72 | 02 Oil/Gas Combustion | Changes/Additions in capacity of existing oil or gas-based combustion turbine plants
|  | Row# | 73 | 03 Hydro | Changes/Additions in capacity of existing Hydropower plants
|  | Row# | 74 | 03 Potential Build Hydro Small | Changes/Additions in capacity of potential Hydropower plants
|  | Row# | 75 | 04 Potential Build Nuclear | Changes/Additions in capacity of potential nuclear power plants
|  | Row# | 76 | 05 Potential Build Interruptible | Changes/Additions in capacity of potential interruptible power plants (these hypothetical plants are used to bridge gap in each of the model regions between demand and supply, including transmission, for that region)
|  | Row# | 77 | 06 Potential Build Solar PV | Changes/Additions in capacity of potential Solar PV power plants
|  | Row# | 78 | 06 Solar PV | Changes/Additions in capacity of existing Solar PV power plants
|  | Row# | 79 | 06 Potential Build Solar PV with storage | Changes/Additions in capacity of potential Solar PV with battery storage power plants
|  | Row# | 80 | 07 Potential Build Biomass Combustion | Changes/Additions in capacity of potential biomass combustion power plants
|  | Row# | 81 | 07 Potential Build Coal | Changes/Additions in capacity of potential coal power plants
|  | Row# | 82 | 08 Potential Build Wind | Changes/Additions in capacity of potential wind power plants
|  | Row# | 83 | Total | Sum of rows 65 to 82
|  | Row# | 86 | 12. Generation by Capacity Reporting Type [GWh] | Block of Rows showing annual generation in GWh from different types of power plants, based on optimized dispatch (Potential build rows shows the generation from new build capacity, as is actually dispatched in the model for this scenario)
|  | Row# | 87 | 01 Potential Build Oil/Gas Combined Cycle | Generation from potential builds of new combined cycle plants
|  | Row# | 88 | 01 Oil/Gas Combined Cycle | Generation from existing and underconstruction combined cycle plants
|  | Row# | 89 | 02 Potential Build Biogas | Generation from potential builds of new biogas plants
|  | Row# | 90 | 02 Gas Combustion Turbine | Generation from existing gas-based combustion turbine plants
|  | Row# | 91 | 02 MSW - Landfill Gas | Generation from existing landfill/MSW plants
|  | Row# | 92 | 02 Oil Combustion | Generation from existing oil-based combustion turbine plants
|  | Row# | 93 | 02 Potential Build Oil/Gas Combustion | Generation from potential builds of oil/gas-based combustion plants (combustion turbines)
|  | Row# | 94 | 02 Oil/Gas Combustion | Generation from existing oil or gas-based combustion turbine plants
|  | Row# | 95 | 03 Hydro | Generation from existing Hydropower plants
|  | Row# | 96 | 03 Potential Build Hydro Small | Generation from potential Hydropower plants
|  | Row# | 97 | 04 Potential Build Nuclear | Generation from potential nuclear power plants
|  | Row# | 98 | 05 Potential Build Interruptible | Generation from potential interruptible power plants (these hypothetical plants are used to bridge gap in each of the model regions between demand and supply, including transmission, for that region)
|  | Row# | 99 | 06 Potential Build Solar PV | Generation from potential Solar PV power plants
|  | Row# | 100 | 06 Solar PV | Generation from existing Solar PV power plants
|  | Row# | 101 | 06 Potential Build Solar PV with storage | Generation from potential Solar PV with battery storage power plants
|  | Row# | 102 | 07 Potential Build Biomass Combustion | Generation from potential biomass combustion power plants
|  | Row# | 103 | 07 Potential Build Coal | Generation from potential coal power plants
|  | Row# | 104 | 08 Potential Build Wind | Generation from potential wind power plants
|  | Row# | 105 | Total | Sum of rows 87 to 104
|  | Row# | 108 | 12a. Generation by Fuel Type [GWh] | Block of Rows showing annual generation in GWh from different types of fuels, based on optimized dispatch
|  | Row# | 109 | Biomass | Generation in GWh from biomass
|  | Row# | 110 | Coal | Generation in GWh from coal
|  | Row# | 111 | Gas | Generation in GWh from natural gas
|  | Row# | 112 | Oil | Generation in GWh from oil-based products (LCO, HFO, LPG, etc)
|  | Row# | 113 | Other | Generation in GWh from other (geothermal, etc.) -- not relevant for Ghana
|  | Row# | 114 | Sun | Generation in GWh from sun
|  | Row# | 115 | Uranium | Generation in GWh from uranium
|  | Row# | 116 | Water | Generation in GWh from water
|  | Row# | 117 | Wind | Generation in GWh from wind
|  | Row# | 118 | Total | Sum of rows 108 to 118
|  | Row# | 120 | 13. Generation by Capacity Reporting Type [TBtu] | Block of Rows showing annual fuel consumed in Tbtu from different types of power plants, based on optimized dispatch (Potential build rows shows the fuel consumed from new build capacity, as is actually dispatched in the model for this scenario)
|  | Row# | 121 | 01 Potential Build Oil/Gas Combined Cycle | Generation in TBtu (using 3412 Btu/kWh) from potential builds of new combined cycle plants
|  | Row# | 122 | 01 Oil/Gas Combined Cycle | Generation in TBtu (using 3412 Btu/kWh) from existing and underconstruction combined cycle plants
|  | Row# | 123 | 02 Potential Build Biogas | Generation in TBtu (using 3412 Btu/kWh) from potential builds of new biogas plants
|  | Row# | 124 | 02 Gas Combustion Turbine | Generation in TBtu (using 3412 Btu/kWh) from existing gas-based combustion turbine plants
|  | Row# | 125 | 02 MSW - Landfill Gas | Generation in TBtu (using 3412 Btu/kWh) from existing landfill/MSW plants
|  | Row# | 126 | 02 Oil Combustion | Generation in TBtu (using 3412 Btu/kWh) from existing oil-based combustion turbine plants
|  | Row# | 127 | 02 Potential Build Oil/Gas Combustion | Generation in TBtu (using 3412 Btu/kWh) from potential builds of oil/gas-based combustion plants (combustion turbines)
|  | Row# | 128 | 02 Oil/Gas Combustion | Generation in TBtu (using 3412 Btu/kWh) from existing oil or gas-based combustion turbine plants
|  | Row# | 129 | 03 Hydro | Generation in TBtu (using 3412 Btu/kWh) from existing Hydropower plants
|  | Row# | 130 | 03 Potential Build Hydro Small | Generation in TBtu (using 3412 Btu/kWh) from potential Hydropower plants
|  | Row# | 131 | 04 Potential Build Nuclear | Generation in TBtu (using 3412 Btu/kWh) from potential nuclear power plants
|  | Row# | 132 | 05 Potential Build Interruptible | Generation in TBtu (using 3412 Btu/kWh) from potential interruptible power plants (these hypothetical plants are used to bridge gap in each of the model regions between demand and supply, including transmission, for that region)
|  | Row# | 133 | 06 Potential Build Solar PV | Generation in TBtu (using 3412 Btu/kWh) from potential Solar PV power plants
|  | Row# | 134 | 06 Solar PV | Generation in TBtu (using 3412 Btu/kWh) from existing Solar PV power plants
|  | Row# | 135 | 06 Potential Build Solar PV with storage | Generation in TBtu (using 3412 Btu/kWh) from potential Solar PV with battery storage power plants
|  | Row# | 136 | 07 Potential Build Biomass Combustion | Generation in TBtu (using 3412 Btu/kWh) from potential biomass combustion power plants
|  | Row# | 137 | 07 Potential Build Coal | Generation in TBtu (using 3412 Btu/kWh) from potential coal power plants
|  | Row# | 138 | 08 Potential Build Wind | Generation in TBtu (using 3412 Btu/kWh) from potential wind power plants
|  | Row# | 139 | Total | Sum of rows 121 to 138
|  | Row# | 142 | 14. Capacity Factor by Capacity Reporting Type [%] | Block of Rows showing annual capaicty factor in % for different types of power plants, based on optimized dispatch for this scenario
|  | Row# | 143 | 01 Potential Build Oil/Gas Combined Cycle | Capacity factor for potential builds of new combined cycle plants
|  | Row# | 144 | 01 Oil/Gas Combined Cycle | Capacity factor for existing and underconstruction combined cycle plants
|  | Row# | 145 | 02 Potential Build Biogas | Capacity factor for potential builds of new biogas plants
|  | Row# | 146 | 02 Gas Combustion Turbine | Capacity factor for existing gas-based combustion turbine plants
|  | Row# | 147 | 02 MSW - Landfill Gas | Capacity factor for existing landfill/MSW plants
|  | Row# | 148 | 02 Oil Combustion | Capacity factor for existing oil-based combustion turbine plants
|  | Row# | 149 | 02 Potential Build Oil/Gas Combustion | Capacity factor for potential builds of oil/gas-based combustion plants (combustion turbines)
|  | Row# | 150 | 02 Oil/Gas Combustion | Capacity factor for existing oil or gas-based combustion turbine plants
|  | Row# | 151 | 03 Hydro | Capacity factor for existing Hydropower plants
|  | Row# | 152 | 03 Potential Build Hydro Small | Capacity factor for potential Hydropower plants
|  | Row# | 153 | 04 Potential Build Nuclear | Capacity factor for potential nuclear power plants
|  | Row# | 154 | 05 Potential Build Interruptible | Capacity factor for potential interruptible power plants (these hypothetical plants are used to bridge gap in each of the model regions between demand and supply, including transmission, for that region)
|  | Row# | 155 | 06 Potential Build Solar PV | Capacity factor for potential Solar PV power plants
|  | Row# | 156 | 06 Solar PV | Capacity factor for existing Solar PV power plants
|  | Row# | 157 | 06 Potential Build Solar PV with storage | Capacity factor for potential Solar PV with battery storage power plants
|  | Row# | 158 | 07 Potential Build Biomass Combustion | Capacity factor for potential biomass combustion power plants
|  | Row# | 159 | 07 Potential Build Coal | Capacity factor for potential coal power plants
|  | Row# | 160 | 08 Potential Build Wind | Capacity factor for potential wind power plants
|  | Row# | 161 | Average | Average capacity factor for Ghana power plants
|  | Row# | 164 | 15. Total Annual Production Cost [Million US2016$](*) | Block of Rows showing annual production cost of electricity in Millions of 2016$
|  | Row# | 165 | Variable O&M | Total variable O&M cost
|  | Row# | 166 | Fixed O&M | Total fixed O&M cost
|  | Row# | 167 | Fuel | Total fuel cost
|  | Row# | 168 | Capital | Total annualized capital cost per year, based on WACC of 10.8% per year
|  | Row# | 169 | Pollutant Transport & Storage | Total pollutant cost (not relevant for Ghana)
|  | Row# | 170 | Total | Sum of rows 165 to 169
|  | Row# | 171 | Sales Revenue | Revenue from sales of electricity (not included in GH-IPM v1.2018)
|  | Row# | 174 | 15c Annual Transmission Activity (*) | Block of Rows showing annual transmission activity
|  | Row# | 175 | [GWh] Transmitted Out Existing Lines | Transmission in GWh out of Ghana on existing lines
|  | Row# | 176 | [GWh] Transmitted Out New Builds | Transmission in GWh out of Ghana on New build lines
|  | Row# | 177 | [MW] Transferred Out Existing Lines | Transmission during Peak demand MW out of Ghana on existing lines
|  | Row# | 178 | [MW] Transferred Out New Builds | Transmission during Peak demand MW out of Ghana on new build lines
|  | Row# | 179 | Book [MW] of Transmission Builds | MW of new transmission builds
|  | Row# | 180 | [GWh] Transmitted Out All Lines | Sum of Row 175+176
|  | Row# | 181 | [MW] Transferred Out All Lines | Sum of Row 177+178
|  | Row# | 184 | 16. Emissions | Block of Rows showing annual emissions from power generation
|  | Row# | 185 | CO2 Thousand Tons | CO2 emissions
|  | Row# | 186 | NOX Thousand Tons | NOX emissions
|  | Row# | 187 | SO2 Thousand Tons | SO2 emissions
|  | Row# | 190 | 17. Fuel Consumption by Fuel and Fuel Type [TBtu] | Block of Rows showing annual fuel consumption from power generation by different fuel types
|  | Row# | 192 | Biomass | Biomass (TBtu) consumption by run year
|  | Row# | 193 | Coal | Coal(TBtu) consumption by run year
|  | Row# | 194 | Gas | Gas (TBtu) consumption by run year
|  | Row# | 195 | Oil | Oil (TBtu) consumption by run year
|  | Row# | 196 | Other | Other (TBtu) consumption by run year
|  | Row# | 197 | Sun | Sun (TBtu) consumption by run year
|  | Row# | 198 | Uranium | Uranium (TBtu) consumption by run year
|  | Row# | 199 | Water | Water (TBtu) consumption by run year
|  | Row# | 200 | Wind | Wind (TBtu) consumption by run year

## RefCase
Back to Contents
| 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
1. Reserve Margin Capacity Annual [MW] | 3348.7611 | 4649.4823 | 4557.3801 | 5131.924 | 5112.044 | 4790.0287 | 5296.4537 | 6338.8277 | 7814.5957
Plus Firm Contract Purchases Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Transmission In Annual [MW] | 173 | 173 | 449.625 | 509.2398 | 619.2034 | 750.3832 | 1145.032 | 1491.2268 | 2285.9044
Less Firm Contract Sales Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Transmission Out Annual [MW] | 273 | 275 | 553.665 | 615.3608 | 732.8542 | 931.7291 | 1417.299 | 1820.5233 | 2636.3411
Total Reserve Margin Capacity Annual [MW] | 3248.7611 | 4547.4823 | 4453.3401 | 5025.803 | 4998.3932 | 4608.6828 | 5024.1867 | 6009.5312 | 7464.159
2. Peak Load Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
Less DSM [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
3. Reserve Margin Annual [%] | 52.8408 | 94.0481 | 78.466 | 87.7536 | 50.7497 | 25.2773 | 17.8785 | 15 | 15
3a.Local Reserves Annual [%] | 157.5454 | 198.4006 | 182.6353 | 191.7181 | 154.1774 | 130.2068 | 124.2665 | 121.3015 | 120.3992
4. Total Generation [GWh] | 13918.8455 | 15531.5321 | 17387.3068 | 17998.0341 | 23370.6913 | 26198.5186 | 30668.0053 | 37352.4686 | 45790.2882
Inter-Region Transmission [GWh] | 378.6315 | 370.9514 | -441.5621 | 355.1281 | -278.1666 | -718.4016 | -1320.2736 | -1622.83 | -1679.9122
Pumping & Storage Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Purchases [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Sales [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Total Supply for Demand [GWh] | 14297.477 | 15902.4834 | 16945.7448 | 18353.1621 | 23092.5247 | 25480.117 | 29347.7317 | 35729.6387 | 44110.376
6. Projected Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
Energy Not Served [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less DSM [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Demand Response [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
7. Dumped Energy [GWh] | 0.001278 | -0.00093765 | 0.0012672 | -0.00043886 | -0.00054617 | -0.00081524 | 0.0049051 | -0.021715 | 0.028562
8. Total Generation [GWh] | 13918.8455 | 15531.5321 | 17387.3068 | 17998.0341 | 23370.6913 | 26198.5186 | 30668.0053 | 37352.4686 | 45790.2882
Less T&D Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9. Total Sales [GWh] | 13918.8455 | 15531.5321 | 17387.3068 | 17998.0341 | 23370.6913 | 26198.5186 | 30668.0053 | 37352.4686 | 45790.2882
10. Capacity by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 524.4097 | 1636.7837 | 3112.5517
01 Oil/Gas Combined Cycle | 1492 | 2160 | 2350 | 2350 | 2350 | 1900 | 1900 | 1900 | 1900
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 455 | 504.92 | 504.92 | 504.92 | 455 | 455 | 455 | 455 | 455
02 MSW - Landfill Gas | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
02 Oil Combustion | 221 | 221 | 221 | 221 | 188.5 | 188.5 | 188.5 | 88.5 | 88.5
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 394.96 | 394.96 | 772.46 | 772.46 | 747.5 | 747.5 | 747.5 | 747.5 | 747.5
03 Hydro | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 80 | 80
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 47.1565 | 147.1565 | 347.1565 | 597.1565 | 1077.1565 | 2347.1565
06 Solar PV | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 1.8
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 145.4386 | 445.4386 | 645.4386 | 945.4386 | 945.4386
Total | 4082.161 | 4887.882 | 5285.4365 | 5355.8751 | 5503.4951 | 5651.4798 | 6587.9048 | 8380.2788 | 11108.0468
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
11. Capacity Additions and Changes by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 486.425 | 1112.374 | 1475.768
01 Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 0 | 100 | 200 | 250 | 480 | 1270
06 Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 75 | 300 | 200 | 300 | 0
Total | 129.301 | 217.102 | 47.1565 | 70.4386 | 255 | 597.9847 | 936.425 | 1892.374 | 2745.768
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
12. Generation by Capacity Reporting Type [GWh]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 299.4711 | 4134.4496 | 12904.3845 | 24539.388
01 Oil/Gas Combined Cycle | 7999.4335 | 10430.076 | 8954.7051 | 9188.7333 | 13444.7034 | 14438.1552 | 14199.0792 | 10900.3447 | 6038.8603
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 366.0331 | 0 | 1813.32 | 0 | 0 | 101.1423 | 149.6612 | 4.5766 | 0.933
02 MSW - Landfill Gas | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446
02 Oil Combustion | 161.4795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 290.4421 | 0 | 1049.8974 | 3075.417 | 3075.4171 | 3075.417 | 3075.417 | 3075.417 | 3075.417
03 Hydro | 5073.9837 | 5073.9824 | 5474.3844 | 5474.3838 | 5974.8823 | 5974.8822 | 5974.884 | 5974.8822 | 5974.8828
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 297.84 | 297.84 | 297.84 | 297.84 | 297.84
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 67.5263 | 67.5263 | 210.7224 | 497.1146 | 855.1048 | 1512.844 | 3204.8034
06 Solar PV | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 2.7132
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 446.76 | 446.76 | 446.76 | 446.76
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8455 | 15531.5321 | 17387.3068 | 17998.0341 | 23370.6913 | 26198.5186 | 30668.0053 | 37352.4686 | 45790.2882
(**) Ind. Boiler generation in BBtu, not included in the total
12a. Generation by Fuel Type [GWh]
Biomass | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 447.5046 | 447.5046 | 447.5046 | 447.5046
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 4935.2716 | 10430.076 | 11817.9225 | 12264.1503 | 16520.1204 | 17914.1856 | 21558.607 | 26884.7228 | 33654.5983
Oil | 3882.1165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 26.7291 | 26.7291 | 94.2553 | 94.2553 | 237.4514 | 523.8436 | 881.8339 | 1539.5731 | 3207.5166
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 5073.9837 | 5073.9824 | 5474.3844 | 5474.3838 | 6272.7223 | 6272.7222 | 6272.724 | 6272.7222 | 6272.7228
Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8455 | 15531.5321 | 17387.3068 | 17998.0341 | 23370.6913 | 26198.5186 | 30668.0053 | 37352.4686 | 45790.2882
13. Generation by Capacity Reporting Type [TBtu]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 1.0218 | 14.1067 | 44.0298 | 83.7284
01 Oil/Gas Combined Cycle | 27.2941 | 35.5874 | 30.5535 | 31.352 | 45.8733 | 49.263 | 48.4473 | 37.192 | 20.6046
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 1.2489 | 0 | 6.187 | 0 | 0 | 0.3451 | 0.51064 | 0.015615 | 0.0031834
02 MSW - Landfill Gas | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406
02 Oil Combustion | 0.55097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0.99099 | 0 | 3.5822 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933
03 Hydro | 17.3124 | 17.3124 | 18.6786 | 18.6786 | 20.3863 | 20.3863 | 20.3863 | 20.3863 | 20.3863
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 1.0162
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 0.2304 | 0.2304 | 0.71898 | 1.6962 | 2.9176 | 5.1618 | 10.9348
06 Solar PV | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0092574
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 1.5243 | 1.5243 | 1.5243 | 1.5243
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 0.56127 | 1.1589 | 3.5494 | 5.143 | 7.5335 | 7.5335
Total | 47.4911 | 52.9936 | 59.3255 | 61.4093 | 79.7408 | 89.3893 | 104.6392 | 127.4466 | 156.2365
(**) Ind. Boiler generation, not included in the total
14. Capacity Factor by Capacity Reporting Type [%]
01 Potential Build Oil/Gas Combined Cycle | N/A | N/A | N/A | N/A | N/A | 89.9999 | 90.0001 | 89.9999 | 90.0001
01 Oil/Gas Combined Cycle | 61.2049 | 55.1226 | 43.499 | 44.6358 | 65.3099 | 86.7469 | 85.3105 | 65.4911 | 36.2825
02 Potential Build Biogas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Gas Combustion Turbine | 9.1834 | 0 | 40.9966 | 0 | 0 | 2.5376 | 3.7549 | 0.11482 | 0.023408
02 MSW - Landfill Gas | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
02 Oil Combustion | 8.3411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Oil/Gas Combustion | 8.3946 | 0 | 15.5155 | 45.449 | 46.9666 | 46.9666 | 46.9666 | 46.9666 | 46.9666
03 Hydro | 42.279 | 42.279 | 45.6153 | 45.6153 | 49.7857 | 49.7857 | 49.7857 | 49.7857 | 49.7857
03 Potential Build Hydro Small | N/A | N/A | N/A | N/A | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
04 Potential Build Nuclear | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
05 Potential Build Interruptible | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
06 Potential Build Solar PV | N/A | N/A | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.0329 | 15.5867
06 Solar PV | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 17.2069
06 Potential Build Solar PV with storage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
07 Potential Build Biomass Combustion | N/A | N/A | N/A | N/A | N/A | 85 | 85 | 85 | 85
07 Potential Build Coal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
08 Potential Build Wind | N/A | N/A | N/A | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594
Average | 38.9232 | 36.2735 | 37.5532 | 38.3611 | 48.4762 | 52.9189 | 53.1415 | 50.8811 | 47.0578
(**) Ind. Boilers not included in the average
15. Total Annual Production Cost [Million US2016$](*)
Variable O&M | 42.9388 | 48.5644 | 53.0709 | 56.0715 | 73.7065 | 80.6913 | 93.4186 | 110.0704 | 127.6875
Fixed O&M | 103.6056 | 148.842 | 161.93 | 165.2202 | 171.1526 | 118.4727 | 141.3111 | 182.8247 | 236.6112
Fuel | 586.7733 | 661.3921 | 831.0153 | 799.3596 | 1086.8287 | 1293.4165 | 1578.074 | 2070.6598 | 2798.3249
Capital | 840.4565 | 1411.163 | 6.3305 | 18.0991 | 86.3254 | 185.2309 | 295.2552 | 505.972 | 776.1312
Pollutant Transport & Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1573.7742 | 2269.9615 | 1052.3468 | 1038.7504 | 1418.0131 | 1677.8115 | 2108.0589 | 2869.5269 | 3938.7549
Sales Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(*) Costs include only those items that are important for determining incremental cost of pollution control (industrial boiler costs are included)
15c Annual Transmission Activity (*)
[GWh] Transmitted Out Existing Lines | 6415.3022 | 9721.808 | 7506.5044 | 11030.2862 | 15789.3647 | 20314.1048 | 19835.6234 | 18977.7075 | 22365.663
[GWh] Transmitted Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[MW] Transferred Out Existing Lines | 273 | 275 | 553.665 | 615.3608 | 732.8542 | 931.7291 | 1417.299 | 1820.5233 | 2636.3411
[MW] Transferred Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Book [MW] of Transmission Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[GWh] Transmitted Out All Lines | 6415.3022 | 9721.808 | 7506.5044 | 11030.2862 | 15789.3647 | 20314.1048 | 19835.6234 | 18977.7075 | 22365.663
[MW] Transferred Out All Lines | 273 | 275 | 553.665 | 615.3608 | 732.8542 | 931.7291 | 1417.299 | 1820.5233 | 2636.3411
16. Emissions
CO2 Thousand Tons | 5292.4783 | 5384.369 | 6516.9419 | 6280.8783 | 8405.9749 | 9160.1444 | 10871.1293 | 13134.975 | 16186.784
NOX Thousand Tons | 24.4838 | 42.2303 | 51.1133 | 49.2618 | 65.9292 | 71.011 | 73.7597 | 67.1133 | 58.6749
SO2 Thousand Tons | 9.5141 | 0.8638 | 1.0455 | 1.0076 | 1.3486 | 1.4695 | 1.744 | 2.1072 | 2.5968
(**) Industrial Boiler emissions are included
17. Fuel Consumption by Fuel and Fuel Type [TBtu]
Fuel Type | 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
Biomass | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 6.0413 | 6.0413 | 6.0413 | 6.0413
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 38.2185 | 82.5263 | 99.8852 | 96.2671 | 128.8385 | 140.3976 | 166.6219 | 201.3199 | 248.095
Oil | 31.3479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## High Demand
Back to Contents
| 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
1. Reserve Margin Capacity Annual [MW] | 3348.7611 | 4653.8273 | 4557.3801 | 5167.4216 | 5302.5466 | 5237.1747 | 6791.4897 | 9290.3477 | 12725.8277
Plus Firm Contract Purchases Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Transmission In Annual [MW] | 173 | 173 | 564.5049 | 613.7685 | 588.5962 | 533.552 | 1614.087 | 2855.768 | 4081.096
Less Firm Contract Sales Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Transmission Out Annual [MW] | 273 | 275 | 668.5449 | 719.8895 | 701.2122 | 571.9696 | 1885.748 | 3184.993 | 4431.486
Total Reserve Margin Capacity Annual [MW] | 3248.7611 | 4551.8273 | 4453.3401 | 5061.3006 | 5189.9306 | 5198.7571 | 6519.8287 | 8961.1227 | 12375.4377
2. Peak Load Annual [MW] | 2125.5848 | 2496.43 | 3024.9083 | 3323.7371 | 3872.3344 | 4520.6582 | 5669.413 | 7792.2804 | 10761.2471
Less DSM [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand Annual [MW] | 2125.5848 | 2496.43 | 3024.9083 | 3323.7371 | 3872.3344 | 4520.6582 | 5669.413 | 7792.2804 | 10761.2471
3. Reserve Margin Annual [%] | 52.8408 | 82.3335 | 47.2223 | 52.2774 | 34.0259 | 15 | 15.0001 | 15 | 15
3a.Local Reserves Annual [%] | 157.5454 | 186.4193 | 150.6618 | 155.4702 | 136.9341 | 115.8498 | 119.7918 | 119.225 | 118.2561
4. Total Generation [GWh] | 13918.8434 | 16638.3259 | 20248.7391 | 22897.7045 | 27150.9521 | 31862.0919 | 40083.919 | 54469.7203 | 74224.9905
Inter-Region Transmission [GWh] | 378.6313 | 370.9514 | 363.1179 | 355.1276 | -278.1664 | -718.4012 | -1320.2727 | -1622.8299 | -1679.9119
Pumping & Storage Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Purchases [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Sales [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Total Supply for Demand [GWh] | 14297.4747 | 17009.2773 | 20611.857 | 23252.8321 | 26872.7857 | 31143.6907 | 38763.6463 | 52846.8903 | 72545.0785
6. Projected Demand [GWh] | 14297.4757 | 17009.2791 | 20611.8585 | 23252.831 | 26872.7864 | 31143.6908 | 38763.6498 | 52846.908 | 72545.1116
Energy Not Served [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less DSM [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Demand Response [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand [GWh] | 14297.4757 | 17009.2791 | 20611.8585 | 23252.831 | 26872.7864 | 31143.6908 | 38763.6498 | 52846.908 | 72545.1116
7. Dumped Energy [GWh] | -0.0010963 | -0.0017455 | -0.0014968 | 0.001115 | -0.0006788 | -0.00011308 | -0.003455 | -0.017622 | -0.033023
8. Total Generation [GWh] | 13918.8434 | 16638.3259 | 20248.7391 | 22897.7045 | 27150.9521 | 31862.0919 | 40083.919 | 54469.7203 | 74224.9905
Less T&D Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9. Total Sales [GWh] | 13918.8434 | 16638.3259 | 20248.7391 | 22897.7045 | 27150.9521 | 31862.0919 | 40083.919 | 54469.7203 | 74224.9905
10. Capacity by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 2019.4457 | 4552.3037 | 7804.7837
01 Oil/Gas Combined Cycle | 1492 | 2160 | 2350 | 2350 | 2350 | 1900 | 1900 | 1900 | 1900
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 455 | 504.92 | 504.92 | 504.92 | 455 | 455 | 455 | 455 | 455
02 MSW - Landfill Gas | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
02 Oil Combustion | 221 | 221 | 221 | 221 | 188.5 | 188.5 | 188.5 | 88.5 | 88.5
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 394.96 | 394.96 | 772.46 | 772.46 | 747.5 | 747.5 | 747.5 | 747.5 | 747.5
03 Hydro | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 80 | 80
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 221.447 | 0 | 35.4976 | 190.5026 | 447.146 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 47.1565 | 147.1565 | 347.1565 | 597.1565 | 1077.1565 | 2347.1565
06 Solar PV | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 1.8
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 730
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 145.4386 | 445.4386 | 645.4386 | 945.4386 | 945.4386
Total | 4082.161 | 4892.227 | 5285.4365 | 5391.3727 | 5693.9977 | 6098.6258 | 8082.9408 | 11415.7988 | 16530.2788
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
11. Capacity Additions and Changes by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 1981.461 | 2532.858 | 3252.48
01 Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 221.447 | 0 | 35.4976 | 190.5026 | 447.146 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 0 | 100 | 200 | 250 | 480 | 1270
06 Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 610
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 75 | 300 | 200 | 300 | 0
Total | 129.301 | 221.447 | 47.1565 | 105.9362 | 445.5026 | 1045.1307 | 2431.461 | 3432.858 | 5132.48
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
12. Generation by Capacity Reporting Type [GWh]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 299.4711 | 15921.2745 | 35890.342 | 59367.5597
01 Oil/Gas Combined Cycle | 7999.4321 | 11536.8693 | 13625.5074 | 14088.4036 | 17224.9644 | 14894.97 | 11967.8199 | 4912.2539 | 810.9905
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 366.0332 | 0 | 25.9024 | 0 | 0 | 3606.9298 | 10.0106 | 0 | 0
02 MSW - Landfill Gas | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446
02 Oil Combustion | 161.4795 | 0 | 0 | 0 | 0 | 57.8922 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 290.4418 | 0 | 1027.9476 | 3075.417 | 3075.4169 | 4718.4951 | 3075.417 | 3047.2785 | 985.4719
03 Hydro | 5073.983 | 5073.9829 | 5474.3818 | 5474.3841 | 5974.8824 | 5974.8829 | 5974.8827 | 5974.8817 | 5974.8826
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 297.84 | 297.84 | 297.84 | 297.84 | 297.84
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 67.5263 | 67.5263 | 210.7224 | 497.1146 | 855.1048 | 1512.844 | 3204.8034
06 Solar PV | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 2.7132
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152.1006 | 925.2786
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 446.76 | 446.76 | 446.76 | 446.76
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8434 | 16638.3259 | 20248.7391 | 22897.7045 | 27150.9521 | 31862.0919 | 40083.919 | 54469.7203 | 74224.9905
(**) Ind. Boiler generation in BBtu, not included in the total
12a. Generation by Fuel Type [GWh]
Biomass | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 447.5046 | 447.5046 | 447.5046 | 447.5046
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 4938.2841 | 11536.8693 | 14600.6264 | 17163.8206 | 20300.3812 | 23519.866 | 30974.522 | 43849.8744 | 46457.8551
Oil | 3879.1026 | 0 | 78.731 | 0 | 0 | 57.8922 | 0 | 0 | 14706.1671
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 26.7291 | 26.7291 | 94.2553 | 94.2553 | 237.4514 | 523.8436 | 881.8339 | 1691.6737 | 4132.7952
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 5073.983 | 5073.9829 | 5474.3818 | 5474.3841 | 6272.7224 | 6272.7229 | 6272.7227 | 6272.7217 | 6272.7226
Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8434 | 16638.3259 | 20248.7391 | 22897.7045 | 27150.9521 | 31862.0919 | 40083.919 | 54469.7203 | 74224.9905
13. Generation by Capacity Reporting Type [TBtu]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 1.0218 | 54.3234 | 122.4578 | 202.5621
01 Oil/Gas Combined Cycle | 27.2941 | 39.3638 | 46.4902 | 48.0696 | 58.7716 | 50.8216 | 40.8342 | 16.7606 | 2.7671
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 1.2489 | 0 | 0.088379 | 0 | 0 | 12.3068 | 0.034156 | 0 | 0
02 MSW - Landfill Gas | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406
02 Oil Combustion | 0.55097 | 0 | 0 | 0 | 0 | 0.19753 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0.99099 | 0 | 3.5074 | 10.4933 | 10.4933 | 16.0995 | 10.4933 | 10.3973 | 3.3624
03 Hydro | 17.3124 | 17.3124 | 18.6786 | 18.6786 | 20.3863 | 20.3863 | 20.3863 | 20.3863 | 20.3863
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 1.0162
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 0.2304 | 0.2304 | 0.71898 | 1.6962 | 2.9176 | 5.1618 | 10.9348
06 Solar PV | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0092574
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51897 | 3.1571
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 1.5243 | 1.5243 | 1.5243 | 1.5243
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 0.56127 | 1.1589 | 3.5494 | 5.143 | 7.5335 | 7.5335
Total | 47.4911 | 56.77 | 69.0887 | 78.127 | 92.639 | 108.7135 | 136.7663 | 185.8507 | 253.2557
(**) Ind. Boiler generation, not included in the total
14. Capacity Factor by Capacity Reporting Type [%]
01 Potential Build Oil/Gas Combined Cycle | N/A | N/A | N/A | N/A | N/A | 89.9999 | 89.9998 | 89.9999 | 86.8329
01 Oil/Gas Combined Cycle | 61.2049 | 60.972 | 66.1882 | 68.4368 | 83.6732 | 89.4915 | 71.9047 | 29.5137 | 4.8726
02 Potential Build Biogas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Gas Combustion Turbine | 9.1834 | 0 | 0.58562 | 0 | 0 | 90.4945 | 0.25116 | 0 | 0
02 MSW - Landfill Gas | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
02 Oil Combustion | 8.3411 | 0 | 0 | 0 | 0 | 3.5059 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Oil/Gas Combustion | 8.3946 | 0 | 15.1912 | 45.449 | 46.9666 | 72.059 | 46.9666 | 46.5368 | 15.0497
03 Hydro | 42.279 | 42.279 | 45.6153 | 45.6153 | 49.7857 | 49.7857 | 49.7857 | 49.7857 | 49.7857
03 Potential Build Hydro Small | N/A | N/A | N/A | N/A | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
04 Potential Build Nuclear | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
05 Potential Build Interruptible | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A
06 Potential Build Solar PV | N/A | N/A | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.0329 | 15.5867
06 Solar PV | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 17.2069
06 Potential Build Solar PV with storage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 14.4692 | 14.4692
07 Potential Build Biomass Combustion | N/A | N/A | N/A | N/A | N/A | 85 | 85 | 85 | 85
07 Potential Build Coal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
08 Potential Build Wind | N/A | N/A | N/A | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594
Average | 38.9232 | 38.8239 | 43.7334 | 48.4829 | 54.4332 | 59.6401 | 56.6105 | 54.4684 | 51.2585
(**) Ind. Boilers not included in the average
15. Total Annual Production Cost [Million US2016$](*)
Variable O&M | 42.9388 | 52.4382 | 65.2631 | 74.5754 | 86.9374 | 104.3104 | 125.344 | 165.2168 | 222.6785
Fixed O&M | 103.6056 | 148.842 | 161.93 | 165.2202 | 171.1526 | 118.4727 | 163.7366 | 229.9175 | 327.4347
Fuel | 586.7732 | 733.609 | 969.3306 | 1153.0871 | 1417.3006 | 1901.4314 | 2279.8324 | 3374.0744 | 5232.8006
Capital | 840.4565 | 1439.4055 | 6.3305 | 248.8335 | 86.3254 | 185.2309 | 463.3391 | 847.7549 | 1388.8167
Pollutant Transport & Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1573.7741 | 2374.2946 | 1202.8542 | 1641.7162 | 1761.7159 | 2309.4454 | 3032.2521 | 4616.9636 | 7171.7304
Sales Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(*) Costs include only those items that are important for determining incremental cost of pollution control (industrial boiler costs are included)
15c Annual Transmission Activity (*)
[GWh] Transmitted Out Existing Lines | 5758.6317 | 10276.6117 | 14847.3718 | 17290.714 | 17215.2834 | 21809.1857 | 22096.0904 | 29686.2057 | 36357.621
[GWh] Transmitted Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 337.7333 | 1070.8483 | 3612.7548
[MW] Transferred Out Existing Lines | 273 | 275 | 668.5449 | 719.8895 | 701.2122 | 571.9696 | 1305.454 | 2055.606 | 2636.295
[MW] Transferred Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 580.294 | 1129.387 | 1795.191
Book [MW] of Transmission Builds | 0 | 0 | 0 | 0 | 0 | 0 | 580.294 | 1129.3868 | 1795.1908
[GWh] Transmitted Out All Lines | 5758.6317 | 10276.6117 | 14847.3718 | 17290.714 | 17215.2834 | 21809.1857 | 22433.8237 | 30757.054 | 39970.3758
[MW] Transferred Out All Lines | 273 | 275 | 668.5449 | 719.8895 | 701.2122 | 571.9696 | 1885.748 | 3184.993 | 4431.486
16. Emissions
CO2 Thousand Tons | 5292.4775 | 5961.354 | 7613.5798 | 8795.5355 | 10504.5472 | 12879.9443 | 15135.5946 | 20920.1683 | 31610.2488
NOX Thousand Tons | 24.4837 | 46.7557 | 59.3431 | 68.9846 | 82.3886 | 99.8359 | 74.41 | 64.2157 | 52.4073
SO2 Thousand Tons | 9.5141 | 0.95637 | 1.4375 | 1.411 | 1.6852 | 2.0748 | 2.4282 | 3.3562 | 39.4914
(**) Industrial Boiler emissions are included
17. Fuel Consumption by Fuel and Fuel Type [TBtu]
Fuel Type | 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
Biomass | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 6.0413 | 6.0413 | 6.0413 | 6.0413
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 38.2185 | 91.3697 | 115.7701 | 134.8093 | 161.0033 | 196.6692 | 231.9834 | 320.6436 | 337.3881
Oil | 31.3479 | 0 | 0.66921 | 0 | 0 | 0.59664 | 0 | 0 | 106.6208
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Low Demand
Back to Contents
| 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
1. Reserve Margin Capacity Annual [MW] | 3348.7611 | 4645.1333 | 4557.3801 | 5131.924 | 5112.044 | 4790.0287 | 5296.4537 | 6338.8277 | 7814.5957
Plus Firm Contract Purchases Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Transmission In Annual [MW] | 173 | 173 | 387.8266 | 388.6985 | 435.8945 | 459.7116 | 609.496 | 755.121 | 881.172
Less Firm Contract Sales Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Transmission Out Annual [MW] | 273 | 275 | 491.8666 | 494.8195 | 549.4105 | 640.9206 | 881.657 | 1084.846 | 1232.062
Total Reserve Margin Capacity Annual [MW] | 3248.7611 | 4543.1333 | 4453.3401 | 5025.803 | 4998.528 | 4608.8197 | 5024.2927 | 6009.1027 | 7463.7057
2. Peak Load Annual [MW] | 2125.5848 | 2290.5298 | 2260.368 | 2238.3094 | 2385.5284 | 2532.6385 | 2747.435 | 3075.7252 | 3434.4983
Less DSM [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand Annual [MW] | 2125.5848 | 2290.5298 | 2260.368 | 2238.3094 | 2385.5284 | 2532.6385 | 2747.435 | 3075.7252 | 3434.4983
3. Reserve Margin Annual [%] | 52.8408 | 98.3442 | 97.0184 | 124.5357 | 109.5355 | 81.977 | 82.8721 | 95.3719 | 117.3157
3a.Local Reserves Annual [%] | 157.5454 | 202.7973 | 201.6212 | 229.2768 | 214.294 | 189.132 | 192.7781 | 206.0921 | 227.5324
4. Total Generation [GWh] | 13918.8443 | 15167.4235 | 15761.0136 | 15631.8339 | 17233.672 | 17833.0808 | 19856.4916 | 22331.2632 | 24762.6173
Inter-Region Transmission [GWh] | 378.6316 | 370.9514 | -441.5621 | -449.5524 | -1082.8465 | -718.4014 | -1320.5627 | -1622.8294 | -1680.6161
Pumping & Storage Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Purchases [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Sales [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Total Supply for Demand [GWh] | 14297.4758 | 15538.375 | 15319.4515 | 15182.2816 | 16150.8255 | 17114.6794 | 18535.9288 | 20708.4338 | 23082.0011
6. Projected Demand [GWh] | 14297.4757 | 15538.3766 | 15319.4508 | 15182.2806 | 16150.8245 | 17114.6789 | 18535.9261 | 20708.4266 | 23081.9991
Energy Not Served [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less DSM [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Demand Response [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand [GWh] | 14297.4757 | 15538.3766 | 15319.4508 | 15182.2806 | 16150.8245 | 17114.6789 | 18535.9261 | 20708.4266 | 23081.9991
7. Dumped Energy [GWh] | 9.6655e-05 | -0.0016213 | 0.00063782 | 0.00094137 | 0.00095683 | 0.00044376 | 0.0027204 | 0.0071467 | 0.0020353
8. Total Generation [GWh] | 13918.8443 | 15167.4235 | 15761.0136 | 15631.8339 | 17233.672 | 17833.0808 | 19856.4916 | 22331.2632 | 24762.6173
Less T&D Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9. Total Sales [GWh] | 13918.8443 | 15167.4235 | 15761.0136 | 15631.8339 | 17233.672 | 17833.0808 | 19856.4916 | 22331.2632 | 24762.6173
10. Capacity by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 524.4097 | 1636.7837 | 3112.5517
01 Oil/Gas Combined Cycle | 1492 | 2160 | 2350 | 2350 | 2350 | 1900 | 1900 | 1900 | 1900
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 455 | 504.92 | 504.92 | 504.92 | 455 | 455 | 455 | 455 | 455
02 MSW - Landfill Gas | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
02 Oil Combustion | 221 | 221 | 221 | 221 | 188.5 | 188.5 | 188.5 | 88.5 | 88.5
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 394.96 | 394.96 | 772.46 | 772.46 | 747.5 | 747.5 | 747.5 | 747.5 | 747.5
03 Hydro | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 80 | 80
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 212.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 47.1565 | 147.1565 | 347.1565 | 597.1565 | 1077.1565 | 2347.1565
06 Solar PV | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 1.8
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 145.4386 | 445.4386 | 645.4386 | 945.4386 | 945.4386
Total | 4082.161 | 4883.533 | 5285.4365 | 5355.8751 | 5503.4951 | 5651.4798 | 6587.9048 | 8380.2788 | 11108.0468
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
11. Capacity Additions and Changes by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 486.425 | 1112.374 | 1475.768
01 Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 212.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 0 | 100 | 200 | 250 | 480 | 1270
06 Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 75 | 300 | 200 | 300 | 0
Total | 129.301 | 212.753 | 47.1565 | 70.4386 | 255 | 597.9847 | 936.425 | 1892.374 | 2745.768
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
12. Generation by Capacity Reporting Type [GWh]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 299.4711 | 4134.4485 | 11114.5983 | 12622.2412
01 Oil/Gas Combined Cycle | 7999.4324 | 10065.967 | 7626.472 | 7147.7164 | 7101.6486 | 6620.6188 | 4560.1238 | 748.2434 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 366.0332 | 0 | 1813.32 | 1813.32 | 206.7795 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0 | 0.7446 | 0.7446 | 0.7446 | 0.7446
02 Oil Combustion | 161.4795 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67512 | 4.6875
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 290.4417 | 0 | 1629.36 | 1629.36 | 3075.417 | 3075.4174 | 2490.2875 | 0 | 0
03 Hydro | 5073.9838 | 5073.9829 | 4596.8616 | 4781.9376 | 5974.883 | 5974.8828 | 5974.8825 | 5974.8828 | 5974.8815
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 297.84 | 297.84 | 297.84 | 297.84 | 297.84
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 67.5263 | 67.5263 | 210.7224 | 497.1146 | 855.1048 | 1512.844 | 3204.8034
06 Solar PV | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 2.7132
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 8.995 | 446.76 | 446.76
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8443 | 15167.4235 | 15761.0136 | 15631.8339 | 17233.672 | 17833.0808 | 19856.4916 | 22331.2632 | 24762.6173
(**) Ind. Boiler generation in BBtu, not included in the total
12a. Generation by Fuel Type [GWh]
Biomass | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0 | 0.7446 | 9.7396 | 447.5046 | 447.5046
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 4938.2847 | 10065.967 | 11069.152 | 10590.3964 | 10383.8451 | 9995.5073 | 11184.8597 | 11862.8417 | 12622.2412
Oil | 3879.1022 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67512 | 4.6875
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 26.7291 | 26.7291 | 94.2553 | 94.2553 | 237.4514 | 523.8436 | 881.8339 | 1539.5731 | 3207.5166
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 5073.9838 | 5073.9829 | 4596.8616 | 4781.9376 | 6272.723 | 6272.7228 | 6272.7225 | 6272.7228 | 6272.7215
Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8443 | 15167.4235 | 15761.0136 | 15631.8339 | 17233.672 | 17833.0808 | 19856.4916 | 22331.2632 | 24762.6173
13. Generation by Capacity Reporting Type [TBtu]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 1.0218 | 14.1067 | 37.923 | 43.0671
01 Oil/Gas Combined Cycle | 27.2941 | 34.3451 | 26.0215 | 24.388 | 24.2308 | 22.5896 | 15.5591 | 2.553 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 1.2489 | 0 | 6.187 | 6.187 | 0.70553 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406
02 Oil Combustion | 0.55097 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0023035 | 0.015994
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0.99099 | 0 | 5.5594 | 5.5594 | 10.4933 | 10.4933 | 8.4969 | 0 | 0
03 Hydro | 17.3124 | 17.3124 | 15.6845 | 16.316 | 20.3863 | 20.3863 | 20.3863 | 20.3863 | 20.3863
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 1.0162
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 0.2304 | 0.2304 | 0.71898 | 1.6962 | 2.9176 | 5.1618 | 10.9348
06 Solar PV | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0092574
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0.030691 | 1.5243 | 1.5243
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 0.56127 | 1.1589 | 3.5494 | 5.143 | 7.5335 | 7.5335
Total | 47.4911 | 51.7512 | 53.7766 | 53.3358 | 58.8013 | 60.8465 | 67.7503 | 76.1943 | 84.4901
(**) Ind. Boiler generation, not included in the total
14. Capacity Factor by Capacity Reporting Type [%]
01 Potential Build Oil/Gas Combined Cycle | N/A | N/A | N/A | N/A | N/A | 89.9999 | 90.0001 | 77.5173 | 46.293
01 Oil/Gas Combined Cycle | 61.2049 | 53.1983 | 37.0469 | 34.7212 | 34.4975 | 39.7778 | 27.398 | 4.4956 | 0
02 Potential Build Biogas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Gas Combustion Turbine | 9.1834 | 0 | 40.9966 | 40.9966 | 5.1879 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 85 | 85 | 85 | 85 | 0 | 85 | 85 | 85 | 85
02 Oil Combustion | 8.3411 | 0 | 0 | 0 | 0 | 0 | 0 | 0.087083 | 0.60464
02 Potential Build Oil/Gas Combustion | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Oil/Gas Combustion | 8.3946 | 0 | 24.0789 | 24.0789 | 46.9666 | 46.9666 | 38.0307 | 0 | 0
03 Hydro | 42.279 | 42.279 | 38.3033 | 39.8455 | 49.7857 | 49.7857 | 49.7857 | 49.7857 | 49.7857
03 Potential Build Hydro Small | N/A | N/A | N/A | N/A | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
04 Potential Build Nuclear | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
05 Potential Build Interruptible | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
06 Potential Build Solar PV | N/A | N/A | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.0329 | 15.5867
06 Solar PV | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 17.2069
06 Potential Build Solar PV with storage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
07 Potential Build Biomass Combustion | N/A | N/A | N/A | N/A | N/A | 0 | 1.7114 | 85 | 85
07 Potential Build Coal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
08 Potential Build Wind | N/A | N/A | N/A | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594
Average | 38.9232 | 35.4547 | 34.0408 | 33.3177 | 35.7466 | 36.0214 | 34.4073 | 30.4194 | 25.4481
(**) Ind. Boilers not included in the average
15. Total Annual Production Cost [Million US2016$](*)
Variable O&M | 42.9388 | 47.29 | 49.1994 | 47.1299 | 44.4775 | 49.7452 | 52.7685 | 51.5452 | 53.1395
Fixed O&M | 103.6056 | 148.842 | 161.93 | 165.2202 | 171.1526 | 118.4727 | 141.3111 | 182.8247 | 236.6112
Fuel | 586.7732 | 638.0447 | 831.0154 | 799.3597 | 653.7175 | 612.04 | 677.0802 | 812.7298 | 1016.6386
Capital | 840.4565 | 1382.8945 | 6.3305 | 18.0991 | 86.3254 | 185.2309 | 295.2552 | 505.972 | 776.1312
Pollutant Transport & Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1573.7741 | 2217.0711 | 1048.4753 | 1029.8089 | 955.6729 | 965.4889 | 1166.4149 | 1553.0717 | 2082.5205
Sales Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(*) Costs include only those items that are important for determining incremental cost of pollution control (industrial boiler costs are included)
15c Annual Transmission Activity (*)
[GWh] Transmitted Out Existing Lines | 6130.4738 | 10414.1781 | 9184.0506 | 9741.6853 | 11412.5949 | 12380.1594 | 16665.6753 | 13135.7914 | 13548.0796
[GWh] Transmitted Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[MW] Transferred Out Existing Lines | 273 | 275 | 491.8666 | 494.8195 | 549.4105 | 640.9206 | 881.657 | 1084.846 | 1232.062
[MW] Transferred Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Book [MW] of Transmission Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[GWh] Transmitted Out All Lines | 6130.4738 | 10414.1781 | 9184.0506 | 9741.6853 | 11412.5949 | 12380.1594 | 16665.6753 | 13135.7914 | 13548.0796
[MW] Transferred Out All Lines | 273 | 275 | 491.8666 | 494.8195 | 549.4105 | 640.9206 | 881.657 | 1084.846 | 1232.062
16. Emissions
CO2 Thousand Tons | 5292.4774 | 5199.0539 | 6516.9423 | 6280.8791 | 5417.0214 | 4975.2407 | 5437.1108 | 5621.3334 | 5974.4838
NOX Thousand Tons | 24.4837 | 40.7769 | 51.1133 | 49.2618 | 42.4864 | 38.1882 | 31.14 | 13.1586 | 11.707
SO2 Thousand Tons | 9.5141 | 0.83407 | 1.0455 | 1.0076 | 0.86904 | 0.79817 | 0.87226 | 0.90173 | 0.95785
(**) Industrial Boiler emissions are included
17. Fuel Consumption by Fuel and Fuel Type [TBtu]
Fuel Type | 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
Biomass | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 0 | 0.010052 | 0.13148 | 6.0413 | 6.0413
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 38.2185 | 79.6859 | 99.8852 | 96.2671 | 83.0267 | 76.2556 | 83.3346 | 86.15 | 91.5112
Oil | 31.3479 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0067012 | 0.048706
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## HighFuelPrice
Back to Contents
| 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
1. Reserve Margin Capacity Annual [MW] | 3348.7611 | 4649.4823 | 4557.3801 | 5131.924 | 5112.044 | 4790.0287 | 5296.4537 | 6338.8277 | 7814.5957
Plus Firm Contract Purchases Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Transmission In Annual [MW] | 173 | 173 | 449.625 | 509.2398 | 618.9336 | 750.2462 | 1144.926 | 1491.1568 | 2285.7662
Less Firm Contract Sales Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Transmission Out Annual [MW] | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
Total Reserve Margin Capacity Annual [MW] | 3248.7611 | 4547.4823 | 4453.3401 | 5025.803 | 4998.528 | 4608.8197 | 5024.2927 | 6009.5316 | 7464.1588
2. Peak Load Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
Less DSM [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
3. Reserve Margin Annual [%] | 52.8408 | 94.0481 | 78.466 | 87.7536 | 50.7538 | 25.281 | 17.881 | 15 | 15
3a.Local Reserves Annual [%] | 157.5454 | 198.4006 | 182.6353 | 191.7181 | 154.1774 | 130.2068 | 124.2665 | 121.3015 | 120.3992
4. Total Generation [GWh] | 13918.8425 | 15531.5309 | 17387.3071 | 17998.0364 | 23370.6908 | 26198.5191 | 30668.0044 | 37352.4711 | 45790.2881
Inter-Region Transmission [GWh] | 378.6318 | 370.9516 | -441.5621 | 355.1277 | -278.1665 | -718.4011 | -1320.2731 | -1622.8298 | -1679.9118
Pumping & Storage Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Purchases [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Sales [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Total Supply for Demand [GWh] | 14297.4742 | 15902.4825 | 16945.745 | 18353.1641 | 23092.5243 | 25480.118 | 29347.7313 | 35729.6413 | 44110.3763
6. Projected Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
Energy Not Served [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less DSM [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Demand Response [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
7. Dumped Energy [GWh] | -0.0015163 | -0.0018965 | 0.0015398 | 0.001506 | -0.00090984 | 0.00016806 | 0.004482 | -0.019057 | 0.028838
8. Total Generation [GWh] | 13918.8425 | 15531.5309 | 17387.3071 | 17998.0364 | 23370.6908 | 26198.5191 | 30668.0044 | 37352.4711 | 45790.2881
Less T&D Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9. Total Sales [GWh] | 13918.8425 | 15531.5309 | 17387.3071 | 17998.0364 | 23370.6908 | 26198.5191 | 30668.0044 | 37352.4711 | 45790.2881
10. Capacity by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 524.4097 | 1636.7837 | 3112.5517
01 Oil/Gas Combined Cycle | 1492 | 2160 | 2350 | 2350 | 2350 | 1900 | 1900 | 1900 | 1900
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 455 | 504.92 | 504.92 | 504.92 | 455 | 455 | 455 | 455 | 455
02 MSW - Landfill Gas | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
02 Oil Combustion | 221 | 221 | 221 | 221 | 188.5 | 188.5 | 188.5 | 88.5 | 88.5
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 394.96 | 394.96 | 772.46 | 772.46 | 747.5 | 747.5 | 747.5 | 747.5 | 747.5
03 Hydro | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 80 | 80
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 47.1565 | 147.1565 | 347.1565 | 597.1565 | 1077.1565 | 2347.1565
06 Solar PV | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 1.8
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 145.4386 | 445.4386 | 645.4386 | 945.4386 | 945.4386
Total | 4082.161 | 4887.882 | 5285.4365 | 5355.8751 | 5503.4951 | 5651.4798 | 6587.9048 | 8380.2788 | 11108.0468
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
11. Capacity Additions and Changes by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 486.425 | 1112.374 | 1475.768
01 Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 0 | 100 | 200 | 250 | 480 | 1270
06 Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 75 | 300 | 200 | 300 | 0
Total | 129.301 | 217.102 | 47.1565 | 70.4386 | 255 | 597.9847 | 936.425 | 1892.374 | 2745.768
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
12. Generation by Capacity Reporting Type [GWh]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 299.4711 | 4134.4489 | 12904.3845 | 24539.388
01 Oil/Gas Combined Cycle | 7999.4308 | 10430.0748 | 8969.4982 | 9188.7352 | 13444.703 | 14438.1544 | 14199.0832 | 10900.3513 | 6038.8617
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 366.0333 | 0 | 1813.32 | 0 | 0 | 101.1435 | 149.6574 | 4.5712 | 0.93205
02 MSW - Landfill Gas | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446
02 Oil Combustion | 161.4795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 290.4422 | 0 | 1035.1044 | 3075.417 | 3075.417 | 3075.417 | 3075.417 | 3075.417 | 3075.417
03 Hydro | 5073.9831 | 5073.9825 | 5474.3846 | 5474.3843 | 5974.8822 | 5974.8824 | 5974.8836 | 5974.8835 | 5974.8823
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 297.84 | 297.84 | 297.84 | 297.84 | 297.84
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 67.5263 | 67.5263 | 210.7224 | 497.1146 | 855.1048 | 1512.844 | 3204.8034
06 Solar PV | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 2.7132
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 446.76 | 446.76 | 446.76 | 446.76
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8425 | 15531.5309 | 17387.3071 | 17998.0364 | 23370.6908 | 26198.5191 | 30668.0044 | 37352.4711 | 45790.2881
(**) Ind. Boiler generation in BBtu, not included in the total
12a. Generation by Fuel Type [GWh]
Biomass | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 447.5046 | 447.5046 | 447.5046 | 447.5046
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 4938.2835 | 10430.0748 | 11817.9226 | 12264.1522 | 16520.12 | 17914.186 | 21558.6065 | 26884.7241 | 33654.5987
Oil | 3879.1022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 26.7291 | 26.7291 | 94.2553 | 94.2553 | 237.4514 | 523.8436 | 881.8339 | 1539.5731 | 3207.5166
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 5073.9831 | 5073.9825 | 5474.3846 | 5474.3843 | 6272.7222 | 6272.7224 | 6272.7236 | 6272.7235 | 6272.7223
Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8425 | 15531.5309 | 17387.3071 | 17998.0364 | 23370.6908 | 26198.5191 | 30668.0044 | 37352.4711 | 45790.2881
13. Generation by Capacity Reporting Type [TBtu]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 1.0218 | 14.1067 | 44.0298 | 83.7284
01 Oil/Gas Combined Cycle | 27.2941 | 35.5874 | 30.6039 | 31.352 | 45.8733 | 49.263 | 48.4473 | 37.192 | 20.6046
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 1.2489 | 0 | 6.187 | 0 | 0 | 0.3451 | 0.51063 | 0.015597 | 0.0031802
02 MSW - Landfill Gas | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406
02 Oil Combustion | 0.55097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0.99099 | 0 | 3.5318 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933
03 Hydro | 17.3124 | 17.3124 | 18.6786 | 18.6786 | 20.3863 | 20.3863 | 20.3863 | 20.3863 | 20.3863
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 1.0162
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 0.2304 | 0.2304 | 0.71898 | 1.6962 | 2.9176 | 5.1618 | 10.9348
06 Solar PV | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0092574
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 1.5243 | 1.5243 | 1.5243 | 1.5243
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 0.56127 | 1.1589 | 3.5494 | 5.143 | 7.5335 | 7.5335
Total | 47.4911 | 52.9936 | 59.3255 | 61.4093 | 79.7408 | 89.3893 | 104.6392 | 127.4466 | 156.2365
(**) Ind. Boiler generation, not included in the total
14. Capacity Factor by Capacity Reporting Type [%]
01 Potential Build Oil/Gas Combined Cycle | N/A | N/A | N/A | N/A | N/A | 89.9999 | 90.0001 | 89.9999 | 90.0001
01 Oil/Gas Combined Cycle | 61.2049 | 55.1226 | 43.5709 | 44.6358 | 65.3099 | 86.7469 | 85.3105 | 65.4912 | 36.2825
02 Potential Build Biogas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Gas Combustion Turbine | 9.1834 | 0 | 40.9966 | 0 | 0 | 2.5376 | 3.7548 | 0.11469 | 0.023384
02 MSW - Landfill Gas | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
02 Oil Combustion | 8.3411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Oil/Gas Combustion | 8.3946 | 0 | 15.2969 | 45.449 | 46.9666 | 46.9666 | 46.9666 | 46.9666 | 46.9666
03 Hydro | 42.279 | 42.279 | 45.6153 | 45.6153 | 49.7857 | 49.7857 | 49.7857 | 49.7857 | 49.7857
03 Potential Build Hydro Small | N/A | N/A | N/A | N/A | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
04 Potential Build Nuclear | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
05 Potential Build Interruptible | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
06 Potential Build Solar PV | N/A | N/A | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.0329 | 15.5867
06 Solar PV | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 17.2069
06 Potential Build Solar PV with storage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
07 Potential Build Biomass Combustion | N/A | N/A | N/A | N/A | N/A | 85 | 85 | 85 | 85
07 Potential Build Coal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
08 Potential Build Wind | N/A | N/A | N/A | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594
Average | 38.9232 | 36.2735 | 37.5532 | 38.3611 | 48.4762 | 52.9189 | 53.1415 | 50.8811 | 47.0578
(**) Ind. Boilers not included in the average
15. Total Annual Production Cost [Million US2016$](*)
Variable O&M | 42.9388 | 48.5644 | 53.0709 | 56.0715 | 73.7065 | 80.6913 | 93.4186 | 110.0705 | 127.7045
Fixed O&M | 103.6056 | 148.842 | 161.93 | 165.2202 | 171.1526 | 118.4727 | 141.3111 | 182.8247 | 236.6112
Fuel | 586.7731 | 661.392 | 831.0153 | 799.3597 | 1188.8239 | 1515.2341 | 1964.1935 | 2774.9127 | 3998.7546
Capital | 840.4565 | 1411.163 | 6.3305 | 18.0991 | 86.3254 | 185.2309 | 295.2552 | 505.972 | 776.1312
Pollutant Transport & Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1573.774 | 2269.9614 | 1052.3468 | 1038.7505 | 1520.0084 | 1899.6291 | 2494.1784 | 3573.7799 | 5139.2016
Sales Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(*) Costs include only those items that are important for determining incremental cost of pollution control (industrial boiler costs are included)
15c Annual Transmission Activity (*)
[GWh] Transmitted Out Existing Lines | 5604.8509 | 9856.3496 | 8106.2166 | 11237.9206 | 13364.7496 | 19808.6853 | 22888.4265 | 18904.0565 | 22083.7061
[GWh] Transmitted Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[MW] Transferred Out Existing Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
[MW] Transferred Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Book [MW] of Transmission Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[GWh] Transmitted Out All Lines | 5604.8509 | 9856.3496 | 8106.2166 | 11237.9206 | 13364.7496 | 19808.6853 | 22888.4265 | 18904.0565 | 22083.7061
[MW] Transferred Out All Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
16. Emissions
CO2 Thousand Tons | 5292.477 | 5384.3682 | 6516.942 | 6280.8793 | 8405.9747 | 9160.1447 | 10871.1288 | 13134.9743 | 16185.9446
NOX Thousand Tons | 24.4837 | 42.2303 | 51.1133 | 49.2618 | 65.9292 | 71.011 | 73.7597 | 67.1132 | 58.6683
SO2 Thousand Tons | 9.5141 | 0.8638 | 1.0455 | 1.0076 | 1.3486 | 1.4695 | 1.744 | 2.1072 | 2.5967
(**) Industrial Boiler emissions are included
17. Fuel Consumption by Fuel and Fuel Type [TBtu]
Fuel Type | 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
Biomass | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 6.0413 | 6.0413 | 6.0413 | 6.0413
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 38.2185 | 82.5263 | 99.8852 | 96.2671 | 128.8385 | 140.3976 | 166.6219 | 201.3199 | 248.0821
Oil | 31.3479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Low Fuel Price
Back to Contents
| 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
1. Reserve Margin Capacity Annual [MW] | 3348.7611 | 4649.4823 | 4557.3801 | 5131.924 | 5112.044 | 4790.0287 | 5296.4537 | 6338.8277 | 7814.5957
Plus Firm Contract Purchases Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Transmission In Annual [MW] | 173 | 173 | 449.625 | 509.2398 | 618.9336 | 750.2462 | 1144.926 | 1491.1568 | 2285.7662
Less Firm Contract Sales Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Transmission Out Annual [MW] | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
Total Reserve Margin Capacity Annual [MW] | 3248.7611 | 4547.4823 | 4453.3401 | 5025.803 | 4998.528 | 4608.8197 | 5024.2927 | 6009.5316 | 7464.1588
2. Peak Load Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
Less DSM [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
3. Reserve Margin Annual [%] | 52.8408 | 94.0481 | 78.466 | 87.7536 | 50.7538 | 25.281 | 17.881 | 15 | 15
3a.Local Reserves Annual [%] | 157.5454 | 198.4006 | 182.6353 | 191.7181 | 154.1774 | 130.2068 | 124.2665 | 121.3015 | 120.3992
4. Total Generation [GWh] | 13918.8449 | 15531.532 | 17387.3071 | 17998.0351 | 23370.6921 | 26198.5206 | 30668.0031 | 37352.4705 | 45790.2896
Inter-Region Transmission [GWh] | 378.6317 | 370.9516 | -441.5621 | 355.1277 | -278.1665 | -718.4012 | -1320.2732 | -1622.8296 | -1679.9118
Pumping & Storage Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Purchases [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Sales [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Total Supply for Demand [GWh] | 14297.4766 | 15902.4836 | 16945.745 | 18353.1628 | 23092.5256 | 25480.1194 | 29347.7299 | 35729.6409 | 44110.3778
6. Projected Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
Energy Not Served [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less DSM [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Demand Response [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
7. Dumped Energy [GWh] | 0.0008393 | -0.00078955 | 0.0014838 | 0.00018804 | 0.0003706 | 0.0016151 | 0.0030661 | -0.01946 | 0.030302
8. Total Generation [GWh] | 13918.8449 | 15531.532 | 17387.3071 | 17998.0351 | 23370.6921 | 26198.5206 | 30668.0031 | 37352.4705 | 45790.2896
Less T&D Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9. Total Sales [GWh] | 13918.8449 | 15531.532 | 17387.3071 | 17998.0351 | 23370.6921 | 26198.5206 | 30668.0031 | 37352.4705 | 45790.2896
10. Capacity by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 524.4097 | 1636.7837 | 3112.5517
01 Oil/Gas Combined Cycle | 1492 | 2160 | 2350 | 2350 | 2350 | 1900 | 1900 | 1900 | 1900
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 455 | 504.92 | 504.92 | 504.92 | 455 | 455 | 455 | 455 | 455
02 MSW - Landfill Gas | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
02 Oil Combustion | 221 | 221 | 221 | 221 | 188.5 | 188.5 | 188.5 | 88.5 | 88.5
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 394.96 | 394.96 | 772.46 | 772.46 | 747.5 | 747.5 | 747.5 | 747.5 | 747.5
03 Hydro | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 80 | 80
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 47.1565 | 147.1565 | 347.1565 | 597.1565 | 1077.1565 | 2347.1565
06 Solar PV | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 1.8
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 145.4386 | 445.4386 | 645.4386 | 945.4386 | 945.4386
Total | 4082.161 | 4887.882 | 5285.4365 | 5355.8751 | 5503.4951 | 5651.4798 | 6587.9048 | 8380.2788 | 11108.0468
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
11. Capacity Additions and Changes by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 486.425 | 1112.374 | 1475.768
01 Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 0 | 100 | 200 | 250 | 480 | 1270
06 Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 75 | 300 | 200 | 300 | 0
Total | 129.301 | 217.102 | 47.1565 | 70.4386 | 255 | 597.9847 | 936.425 | 1892.374 | 2745.768
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
12. Generation by Capacity Reporting Type [GWh]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 299.4711 | 4134.4496 | 12904.3843 | 24539.388
01 Oil/Gas Combined Cycle | 8045.9575 | 10430.8214 | 8979.1541 | 9188.7347 | 13444.7036 | 14671.0428 | 14483.0689 | 11341.1937 | 6038.8676
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 328.699 | 0 | 1813.32 | 0 | 0 | 315.015 | 303.4359 | 10.4886 | 0.93205
02 MSW - Landfill Gas | 0.7446 | 0 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446
02 Oil Combustion | 115.6521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 327.0791 | 0 | 1025.4492 | 3075.4168 | 3075.417 | 3075.417 | 3075.417 | 3075.417 | 3075.417
03 Hydro | 5073.9835 | 5073.9816 | 5474.3838 | 5474.3837 | 5974.883 | 5974.8839 | 5974.8824 | 5974.8833 | 5974.8832
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 297.84 | 297.84 | 297.84 | 297.84 | 297.84
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 67.5263 | 67.5263 | 210.7224 | 497.1146 | 855.1048 | 1512.844 | 3204.8034
06 Solar PV | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 2.7132
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 8.995 | 0 | 446.7547
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8449 | 15531.532 | 17387.3071 | 17998.0351 | 23370.6921 | 26198.5206 | 30668.0031 | 37352.4705 | 45790.2896
(**) Ind. Boiler generation in BBtu, not included in the total
12a. Generation by Fuel Type [GWh]
Biomass | 0.7446 | 0 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 9.7396 | 0.7446 | 447.4993
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 4947.4748 | 10065.3452 | 11817.9233 | 12264.1514 | 16520.1206 | 18360.9459 | 21996.3714 | 27331.4836 | 33654.6046
Oil | 3869.9129 | 365.4762 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 26.7291 | 26.7291 | 94.2553 | 94.2553 | 237.4514 | 523.8436 | 881.8339 | 1539.5731 | 3207.5166
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 5073.9835 | 5073.9816 | 5474.3838 | 5474.3837 | 6272.723 | 6272.7239 | 6272.7224 | 6272.7233 | 6272.7232
Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8449 | 15531.532 | 17387.3071 | 17998.0351 | 23370.6921 | 26198.5206 | 30668.0031 | 37352.4705 | 45790.2896
13. Generation by Capacity Reporting Type [TBtu]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 1.0218 | 14.1067 | 44.0298 | 83.7284
01 Oil/Gas Combined Cycle | 27.4528 | 35.59 | 30.6369 | 31.352 | 45.8733 | 50.0576 | 49.4162 | 38.6962 | 20.6046
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 1.1215 | 0 | 6.187 | 0 | 0 | 1.0748 | 1.0353 | 0.035787 | 0.0031802
02 MSW - Landfill Gas | 0.0025406 | 0 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406
02 Oil Combustion | 0.39461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 1.116 | 0 | 3.4988 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933
03 Hydro | 17.3124 | 17.3124 | 18.6786 | 18.6786 | 20.3863 | 20.3863 | 20.3863 | 20.3863 | 20.3863
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 1.0162
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 0.2304 | 0.2304 | 0.71898 | 1.6962 | 2.9176 | 5.1618 | 10.9348
06 Solar PV | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0092574
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0.030691 | 0 | 1.5243
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 0.56127 | 1.1589 | 3.5494 | 5.143 | 7.5335 | 7.5335
Total | 47.4911 | 52.9936 | 59.3255 | 61.4093 | 79.7408 | 89.3894 | 104.6392 | 127.4466 | 156.2365
(**) Ind. Boiler generation, not included in the total
14. Capacity Factor by Capacity Reporting Type [%]
01 Potential Build Oil/Gas Combined Cycle | N/A | N/A | N/A | N/A | N/A | 89.9999 | 90.0001 | 89.9999 | 90.0001
01 Oil/Gas Combined Cycle | 61.5609 | 55.1265 | 43.6178 | 44.6358 | 65.3099 | 88.1461 | 87.0168 | 68.1398 | 36.2825
02 Potential Build Biogas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Gas Combustion Turbine | 8.2468 | 0 | 40.9966 | 0 | 0 | 7.9034 | 7.6129 | 0.26315 | 0.023384
02 MSW - Landfill Gas | 85 | 0 | 85 | 85 | 85 | 85 | 85 | 85 | 85
02 Oil Combustion | 5.9739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Oil/Gas Combustion | 9.4536 | 0 | 15.1542 | 45.449 | 46.9666 | 46.9666 | 46.9666 | 46.9666 | 46.9666
03 Hydro | 42.279 | 42.279 | 45.6153 | 45.6153 | 49.7857 | 49.7857 | 49.7857 | 49.7857 | 49.7857
03 Potential Build Hydro Small | N/A | N/A | N/A | N/A | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
04 Potential Build Nuclear | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
05 Potential Build Interruptible | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
06 Potential Build Solar PV | N/A | N/A | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.0329 | 15.5867
06 Solar PV | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 17.2069
06 Potential Build Solar PV with storage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
07 Potential Build Biomass Combustion | N/A | N/A | N/A | N/A | N/A | 0 | 1.7114 | 0 | 84.999
07 Potential Build Coal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
08 Potential Build Wind | N/A | N/A | N/A | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594
Average | 38.9232 | 36.2735 | 37.5532 | 38.3611 | 48.4762 | 52.9189 | 53.1415 | 50.8811 | 47.0578
(**) Ind. Boilers not included in the average
15. Total Annual Production Cost [Million US2016$](*)
Variable O&M | 42.8084 | 48.5639 | 53.0709 | 55.376 | 73.7065 | 80.4584 | 93.1346 | 110.0428 | 127.6875
Fixed O&M | 103.6056 | 148.842 | 161.93 | 165.2202 | 171.1526 | 118.4727 | 141.3111 | 182.8247 | 236.6112
Fuel | 496.4302 | 492.6995 | 631.2453 | 607.5172 | 721.7409 | 821.2875 | 1003.9917 | 1355.0268 | 1808.2005
Capital | 840.4565 | 1411.163 | 6.3305 | 18.0991 | 86.3254 | 185.2309 | 295.2552 | 505.972 | 776.1312
Pollutant Transport & Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1483.3006 | 2101.2684 | 852.5768 | 846.2125 | 1052.9253 | 1205.4496 | 1533.6926 | 2153.8663 | 2948.6305
Sales Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(*) Costs include only those items that are important for determining incremental cost of pollution control (industrial boiler costs are included)
15c Annual Transmission Activity (*)
[GWh] Transmitted Out Existing Lines | 7662.7611 | 11993.797 | 8854.4084 | 11219.8642 | 16328.9546 | 18996.2149 | 20102.9372 | 19071.2622 | 21042.8608
[GWh] Transmitted Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[MW] Transferred Out Existing Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
[MW] Transferred Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Book [MW] of Transmission Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[GWh] Transmitted Out All Lines | 7662.7611 | 11993.797 | 8854.4084 | 11219.8642 | 16328.9546 | 18996.2149 | 20102.9372 | 19071.2622 | 21042.8608
[MW] Transferred Out All Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
16. Emissions
CO2 Thousand Tons | 5293.7633 | 5478.8557 | 6516.9423 | 6290.2026 | 8405.975 | 9419.489 | 11122.2304 | 13372.9652 | 16186.7852
NOX Thousand Tons | 24.4852 | 41.245 | 51.1133 | 49.3349 | 65.9292 | 73.0451 | 75.7292 | 68.9798 | 58.6749
SO2 Thousand Tons | 9.5173 | 1.8835 | 1.0455 | 1.0091 | 1.3486 | 1.5111 | 1.7843 | 2.1454 | 2.5968
(**) Industrial Boiler emissions are included
17. Fuel Consumption by Fuel and Fuel Type [TBtu]
Fuel Type | 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
Biomass | 0.010052 | 0 | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 0.13148 | 0.010052 | 6.0412
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 38.2185 | 79.6814 | 99.8852 | 96.41 | 128.8385 | 144.3726 | 170.4705 | 204.9676 | 248.095
Oil | 31.3622 | 3.1117 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Limited Fuel Supply
Back to Contents
| 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
1. Reserve Margin Capacity Annual [MW] | 3348.7611 | 4649.4823 | 4557.3801 | 5131.924 | 5112.044 | 4790.0287 | 5296.4537 | 6338.8277 | 7814.5957
Plus Firm Contract Purchases Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Transmission In Annual [MW] | 173 | 173 | 449.625 | 509.2398 | 618.9336 | 750.2462 | 1144.926 | 1491.1568 | 2285.7662
Less Firm Contract Sales Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Transmission Out Annual [MW] | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
Total Reserve Margin Capacity Annual [MW] | 3248.7611 | 4547.4823 | 4453.3401 | 5025.803 | 4998.528 | 4608.8197 | 5024.2927 | 6009.5316 | 7464.1588
2. Peak Load Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
Less DSM [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
3. Reserve Margin Annual [%] | 52.8408 | 94.0481 | 78.466 | 87.7536 | 50.7538 | 25.281 | 17.881 | 15 | 15
3a.Local Reserves Annual [%] | 157.5454 | 198.4006 | 182.6353 | 191.7181 | 154.1774 | 130.2068 | 124.2665 | 121.3015 | 120.3992
4. Total Generation [GWh] | 13918.8431 | 15531.5314 | 16582.6261 | 17998.0362 | 23370.69 | 26198.5193 | 30668.0041 | 37352.4677 | 45790.2896
Inter-Region Transmission [GWh] | 378.6317 | 370.9513 | 363.1179 | 355.1274 | -278.1664 | -718.4015 | -1320.2728 | -1622.8296 | -1679.9117
Pumping & Storage Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Purchases [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Sales [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Total Supply for Demand [GWh] | 14297.4748 | 15902.4827 | 16945.744 | 18353.1636 | 23092.5236 | 25480.1177 | 29347.7312 | 35729.6382 | 44110.3779
6. Projected Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
Energy Not Served [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less DSM [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Demand Response [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
7. Dumped Energy [GWh] | -0.00094909 | -0.0016978 | 0.00049824 | 0.0010487 | -0.0016014 | -7.3652e-05 | 0.0044115 | -0.022206 | 0.030435
8. Total Generation [GWh] | 13918.8431 | 15531.5314 | 16582.6261 | 17998.0362 | 23370.69 | 26198.5193 | 30668.0041 | 37352.4677 | 45790.2896
Less T&D Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9. Total Sales [GWh] | 13918.8431 | 15531.5314 | 16582.6261 | 17998.0362 | 23370.69 | 26198.5193 | 30668.0041 | 37352.4677 | 45790.2896
10. Capacity by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 524.4097 | 1636.7837 | 3112.5517
01 Oil/Gas Combined Cycle | 1492 | 2160 | 2350 | 2350 | 2350 | 1900 | 1900 | 1900 | 1900
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 455 | 504.92 | 504.92 | 504.92 | 455 | 455 | 455 | 455 | 455
02 MSW - Landfill Gas | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
02 Oil Combustion | 221 | 221 | 221 | 221 | 188.5 | 188.5 | 188.5 | 88.5 | 88.5
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 394.96 | 394.96 | 772.46 | 772.46 | 747.5 | 747.5 | 747.5 | 747.5 | 747.5
03 Hydro | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 80 | 80
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 47.1565 | 147.1565 | 347.1565 | 597.1565 | 1077.1565 | 2347.1565
06 Solar PV | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 1.8
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 145.4386 | 445.4386 | 645.4386 | 945.4386 | 945.4386
Total | 4082.161 | 4887.882 | 5285.4365 | 5355.8751 | 5503.4951 | 5651.4798 | 6587.9048 | 8380.2788 | 11108.0468
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
11. Capacity Additions and Changes by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 486.425 | 1112.374 | 1475.768
01 Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 0 | 100 | 200 | 250 | 480 | 1270
06 Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 75 | 300 | 200 | 300 | 0
Total | 129.301 | 217.102 | 47.1565 | 70.4386 | 255 | 597.9847 | 936.425 | 1892.374 | 2745.768
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
12. Generation by Capacity Reporting Type [GWh]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 299.4711 | 4134.4502 | 12904.3823 | 24539.388
01 Oil/Gas Combined Cycle | 7999.4312 | 10430.0744 | 9985.2949 | 9188.7348 | 13444.7026 | 14438.1533 | 14199.0825 | 10900.351 | 7333.1812
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 109.4187 | 0 | 0 | 0 | 0 | 101.1435 | 149.6574 | 4.5712 | 0.93205
02 MSW - Landfill Gas | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446
02 Oil Combustion | 161.4795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 547.0559 | 0 | 1027.9476 | 3075.417 | 3075.417 | 3075.417 | 3075.417 | 3075.417 | 1781.0986
03 Hydro | 5073.9841 | 5073.9833 | 5474.3836 | 5474.3845 | 5974.882 | 5974.8836 | 5974.8827 | 5974.8826 | 5974.8828
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 297.84 | 297.84 | 297.84 | 297.84 | 297.84
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 67.5263 | 67.5263 | 210.7224 | 497.1146 | 855.1048 | 1512.844 | 3204.8034
06 Solar PV | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 2.7132
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 446.76 | 446.76 | 446.76 | 446.76
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8431 | 15531.5314 | 16582.6261 | 17998.0362 | 23370.69 | 26198.5193 | 30668.0041 | 37352.4677 | 45790.2896
(**) Ind. Boiler generation in BBtu, not included in the total
12a. Generation by Fuel Type [GWh]
Biomass | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 447.5046 | 447.5046 | 447.5046 | 447.5046
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 4676.8965 | 9953.6768 | 11013.2425 | 11317.8183 | 11306.814 | 9896.8632 | 9173.3649 | 6248.6769 | 2036.1817
Oil | 4140.4888 | 476.3976 | 0 | 946.3335 | 5213.3056 | 8017.3217 | 12385.2421 | 20636.0446 | 31618.4181
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 26.7291 | 26.7291 | 94.2553 | 94.2553 | 237.4514 | 523.8436 | 881.8339 | 1539.5731 | 3207.5166
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 5073.9841 | 5073.9833 | 5474.3836 | 5474.3845 | 6272.722 | 6272.7236 | 6272.7227 | 6272.7226 | 6272.7228
Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8431 | 15531.5314 | 16582.6261 | 17998.0362 | 23370.69 | 26198.5193 | 30668.0041 | 37352.4677 | 45790.2896
13. Generation by Capacity Reporting Type [TBtu]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 1.0218 | 14.1067 | 44.0298 | 83.7284
01 Oil/Gas Combined Cycle | 27.2941 | 35.5874 | 34.0698 | 31.352 | 45.8733 | 49.263 | 48.4473 | 37.192 | 25.0208
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0.37334 | 0 | 0 | 0 | 0 | 0.3451 | 0.51063 | 0.015597 | 0.0031802
02 MSW - Landfill Gas | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406
02 Oil Combustion | 0.55097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 1.8666 | 0 | 3.5074 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 6.0771
03 Hydro | 17.3124 | 17.3124 | 18.6786 | 18.6786 | 20.3863 | 20.3863 | 20.3863 | 20.3863 | 20.3863
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 1.0162
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 0.2304 | 0.2304 | 0.71898 | 1.6962 | 2.9176 | 5.1618 | 10.9348
06 Solar PV | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0092574
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 1.5243 | 1.5243 | 1.5243 | 1.5243
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 0.56127 | 1.1589 | 3.5494 | 5.143 | 7.5335 | 7.5335
Total | 47.4911 | 52.9936 | 56.5799 | 61.4093 | 79.7408 | 89.3893 | 104.6392 | 127.4466 | 156.2365
(**) Ind. Boiler generation, not included in the total
14. Capacity Factor by Capacity Reporting Type [%]
01 Potential Build Oil/Gas Combined Cycle | N/A | N/A | N/A | N/A | N/A | 89.9999 | 90.0001 | 89.9999 | 90.0001
01 Oil/Gas Combined Cycle | 61.2049 | 55.1226 | 48.5053 | 44.6358 | 65.3099 | 86.7469 | 85.3105 | 65.4912 | 44.059
02 Potential Build Biogas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Gas Combustion Turbine | 2.7452 | 0 | 0 | 0 | 0 | 2.5376 | 3.7548 | 0.11469 | 0.023384
02 MSW - Landfill Gas | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
02 Oil Combustion | 8.3411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Oil/Gas Combustion | 15.8116 | 0 | 15.1912 | 45.449 | 46.9666 | 46.9666 | 46.9666 | 46.9666 | 27.2002
03 Hydro | 42.279 | 42.279 | 45.6153 | 45.6153 | 49.7857 | 49.7857 | 49.7857 | 49.7857 | 49.7857
03 Potential Build Hydro Small | N/A | N/A | N/A | N/A | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
04 Potential Build Nuclear | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
05 Potential Build Interruptible | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
06 Potential Build Solar PV | N/A | N/A | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.0329 | 15.5867
06 Solar PV | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 17.2069
06 Potential Build Solar PV with storage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
07 Potential Build Biomass Combustion | N/A | N/A | N/A | N/A | N/A | 85 | 85 | 85 | 85
07 Potential Build Coal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
08 Potential Build Wind | N/A | N/A | N/A | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594
Average | 38.9232 | 36.2735 | 35.8153 | 38.3611 | 48.4762 | 52.9189 | 53.1415 | 50.8811 | 47.0578
(**) Ind. Boilers not included in the average
15. Total Annual Production Cost [Million US2016$](*)
Variable O&M | 42.6822 | 48.5644 | 52.3799 | 57.4266 | 71.7748 | 80.0595 | 92.5559 | 109.7153 | 132.0791
Fixed O&M | 103.6056 | 148.842 | 161.93 | 165.2202 | 171.1526 | 118.4727 | 141.3111 | 182.8247 | 236.6112
Fuel | 600.6945 | 666.6268 | 712.1175 | 810.9541 | 1180.5882 | 1502.7009 | 1896.7236 | 2494.7643 | 3340.7381
Capital | 840.4565 | 1411.163 | 6.3305 | 18.0991 | 86.3254 | 185.2309 | 295.2552 | 505.972 | 776.1312
Pollutant Transport & Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1587.4387 | 2275.1962 | 932.7579 | 1051.7 | 1509.8409 | 1886.4641 | 2425.8459 | 3293.2763 | 4485.5597
Sales Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(*) Costs include only those items that are important for determining incremental cost of pollution control (industrial boiler costs are included)
15c Annual Transmission Activity (*)
[GWh] Transmitted Out Existing Lines | 7236.7065 | 12540.6158 | 11254.3893 | 12750.5945 | 16040.4747 | 13922.023 | 19935.8425 | 17733.9759 | 24661.5715
[GWh] Transmitted Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[MW] Transferred Out Existing Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
[MW] Transferred Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Book [MW] of Transmission Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[GWh] Transmitted Out All Lines | 7236.7065 | 12540.6158 | 11254.3893 | 12750.5945 | 16040.4747 | 13922.023 | 19935.8425 | 17733.9759 | 24661.5715
[MW] Transferred Out All Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
16. Emissions
CO2 Thousand Tons | 5387.1019 | 5462.1576 | 5591.8658 | 6425.6772 | 9632.8471 | 10599.4463 | 13089.7686 | 16928.5881 | 21958.1653
NOX Thousand Tons | 23.5331 | 40.5901 | 43.8578 | 45.9272 | 50.9369 | 51.294 | 50.4137 | 40.0438 | 25.5905
SO2 Thousand Tons | 10.1178 | 2.1857 | 0.89709 | 3.6319 | 15.8679 | 14.9722 | 24.828 | 45.4438 | 72.8365
(**) Industrial Boiler emissions are included
17. Fuel Consumption by Fuel and Fuel Type [TBtu]
Fuel Type | 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
Biomass | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 6.0413 | 6.0413 | 6.0413 | 6.0413
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 35.8097 | 78.1225 | 85.7066 | 87.3702 | 86.4325 | 75.7458 | 70.0604 | 47.1924 | 15.2872
Oil | 34.145 | 4.056 | 0 | 8.0571 | 44.3655 | 64.7909 | 96.7997 | 155.7765 | 234.4762
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Greater Fuel Supply
Back to Contents
| 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
1. Reserve Margin Capacity Annual [MW] | 3348.7611 | 4649.4823 | 4557.3801 | 5131.924 | 5112.044 | 4790.0287 | 5296.4537 | 6338.8277 | 7814.5957
Plus Firm Contract Purchases Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Transmission In Annual [MW] | 173 | 173 | 449.625 | 509.2398 | 618.9336 | 750.2462 | 1144.926 | 1491.1568 | 2285.7662
Less Firm Contract Sales Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Transmission Out Annual [MW] | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
Total Reserve Margin Capacity Annual [MW] | 3248.7611 | 4547.4823 | 4453.3401 | 5025.803 | 4998.528 | 4608.8197 | 5024.2927 | 6009.5316 | 7464.1588
2. Peak Load Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
Less DSM [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
3. Reserve Margin Annual [%] | 52.8408 | 94.0481 | 78.466 | 87.7536 | 50.7538 | 25.281 | 17.881 | 15 | 15
3a.Local Reserves Annual [%] | 157.5454 | 198.4006 | 182.6353 | 191.7181 | 154.1774 | 130.2068 | 124.2665 | 121.3015 | 120.3992
4. Total Generation [GWh] | 13918.8449 | 15556.7809 | 17387.3078 | 18802.7155 | 24101.3789 | 26198.5172 | 30668.0017 | 37352.4713 | 45790.2869
Inter-Region Transmission [GWh] | 378.6315 | 345.7016 | -441.5621 | -449.5524 | -1008.8534 | -718.4015 | -1320.2729 | -1622.8298 | -1679.9115
Pumping & Storage Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Purchases [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Sales [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Total Supply for Demand [GWh] | 14297.4764 | 15902.4825 | 16945.7457 | 18353.1631 | 23092.5256 | 25480.1158 | 29347.7288 | 35729.6414 | 44110.3754
6. Projected Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
Energy Not Served [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less DSM [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Demand Response [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
7. Dumped Energy [GWh] | 0.00060625 | -0.0018816 | 0.0022328 | 0.00054469 | 0.00033752 | -0.0020378 | 0.001973 | -0.01893 | 0.027978
8. Total Generation [GWh] | 13918.8449 | 15556.7809 | 17387.3078 | 18802.7155 | 24101.3789 | 26198.5172 | 30668.0017 | 37352.4713 | 45790.2869
Less T&D Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9. Total Sales [GWh] | 13918.8449 | 15556.7809 | 17387.3078 | 18802.7155 | 24101.3789 | 26198.5172 | 30668.0017 | 37352.4713 | 45790.2869
10. Capacity by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 524.4097 | 1636.7837 | 3112.5517
01 Oil/Gas Combined Cycle | 1492 | 2160 | 2350 | 2350 | 2350 | 1900 | 1900 | 1900 | 1900
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 455 | 504.92 | 504.92 | 504.92 | 455 | 455 | 455 | 455 | 455
02 MSW - Landfill Gas | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
02 Oil Combustion | 221 | 221 | 221 | 221 | 188.5 | 188.5 | 188.5 | 88.5 | 88.5
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 394.96 | 394.96 | 772.46 | 772.46 | 747.5 | 747.5 | 747.5 | 747.5 | 747.5
03 Hydro | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 80 | 80
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 47.1565 | 147.1565 | 347.1565 | 597.1565 | 1077.1565 | 2347.1565
06 Solar PV | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 1.8
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 145.4386 | 445.4386 | 645.4386 | 945.4386 | 945.4386
Total | 4082.161 | 4887.882 | 5285.4365 | 5355.8751 | 5503.4951 | 5651.4798 | 6587.9048 | 8380.2788 | 11108.0468
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
11. Capacity Additions and Changes by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 486.425 | 1112.374 | 1475.768
01 Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 0 | 100 | 200 | 250 | 480 | 1270
06 Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 75 | 300 | 200 | 300 | 0
Total | 129.301 | 217.102 | 47.1565 | 70.4386 | 255 | 597.9847 | 936.425 | 1892.374 | 2745.768
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
12. Generation by Capacity Reporting Type [GWh]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 299.4711 | 4134.4483 | 12904.3844 | 24539.388
01 Oil/Gas Combined Cycle | 8240.3414 | 10456.0687 | 9301.3165 | 9845.5358 | 14176.1354 | 14438.1525 | 14199.0824 | 10900.3513 | 6038.8606
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 521.3863 | 0 | 1813.32 | 1813.32 | 0 | 101.1435 | 149.6574 | 4.5712 | 0.93205
02 MSW - Landfill Gas | 0.7446 | 0 | 0.7446 | 0.7446 | 0 | 0.7446 | 0.7446 | 0.7446 | 0.7446
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 55.6601 | 0 | 1629.36 | 1629.36 | 3075.417 | 3075.417 | 3075.417 | 3075.417 | 3075.417
03 Hydro | 5073.9834 | 5073.9831 | 4548.3113 | 5254.9997 | 5974.8826 | 5974.8824 | 5974.8824 | 5974.8837 | 5974.8822
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 297.84 | 297.84 | 297.84 | 297.84 | 297.84
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 67.5263 | 67.5263 | 210.7224 | 497.1146 | 855.1048 | 1512.844 | 3204.8034
06 Solar PV | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 2.7132
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 446.76 | 446.76 | 446.76 | 446.76
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8449 | 15556.7809 | 17387.3078 | 18802.7155 | 24101.3789 | 26198.5172 | 30668.0017 | 37352.4713 | 45790.2869
(**) Ind. Boiler generation in BBtu, not included in the total
12a. Generation by Fuel Type [GWh]
Biomass | 0.7446 | 0 | 0.7446 | 0.7446 | 0 | 447.5046 | 447.5046 | 447.5046 | 447.5046
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 6096.719 | 10456.0687 | 12743.9965 | 13288.2158 | 17251.5524 | 17914.1841 | 21558.605 | 26884.724 | 33654.5976
Oil | 2720.6688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 26.7291 | 26.7291 | 94.2553 | 94.2553 | 237.4514 | 523.8436 | 881.8339 | 1539.5731 | 3207.5166
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 5073.9834 | 5073.9831 | 4548.3113 | 5254.9997 | 6272.7226 | 6272.7224 | 6272.7224 | 6272.7237 | 6272.7222
Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8449 | 15556.7809 | 17387.3078 | 18802.7155 | 24101.3789 | 26198.5172 | 30668.0017 | 37352.4713 | 45790.2869
13. Generation by Capacity Reporting Type [TBtu]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 1.0218 | 14.1067 | 44.0298 | 83.7284
01 Oil/Gas Combined Cycle | 28.116 | 35.6761 | 31.7361 | 33.593 | 48.369 | 49.263 | 48.4473 | 37.192 | 20.6046
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 1.779 | 0 | 6.187 | 6.187 | 0 | 0.3451 | 0.51063 | 0.015597 | 0.0031802
02 MSW - Landfill Gas | 0.0025406 | 0 | 0.0025406 | 0.0025406 | 0 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0.18991 | 0 | 5.5594 | 5.5594 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933
03 Hydro | 17.3124 | 17.3124 | 15.5188 | 17.9301 | 20.3863 | 20.3863 | 20.3863 | 20.3863 | 20.3863
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 1.0162
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 0.2304 | 0.2304 | 0.71898 | 1.6962 | 2.9176 | 5.1618 | 10.9348
06 Solar PV | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0092574
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 1.5243 | 1.5243 | 1.5243 | 1.5243
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 0.56127 | 1.1589 | 3.5494 | 5.143 | 7.5335 | 7.5335
Total | 47.4911 | 53.0797 | 59.3255 | 64.1549 | 82.2339 | 89.3893 | 104.6392 | 127.4466 | 156.2365
(**) Ind. Boiler generation, not included in the total
14. Capacity Factor by Capacity Reporting Type [%]
01 Potential Build Oil/Gas Combined Cycle | N/A | N/A | N/A | N/A | N/A | 89.9999 | 90 | 89.9999 | 90.0001
01 Oil/Gas Combined Cycle | 63.0481 | 55.26 | 45.1827 | 47.8264 | 68.863 | 86.7469 | 85.3105 | 65.4912 | 36.2825
02 Potential Build Biogas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Gas Combustion Turbine | 13.0811 | 0 | 40.9966 | 40.9966 | 0 | 2.5376 | 3.7548 | 0.11469 | 0.023384
02 MSW - Landfill Gas | 85 | 0 | 85 | 85 | 0 | 85 | 85 | 85 | 85
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Oil/Gas Combustion | 1.6087 | 0 | 24.0789 | 24.0789 | 46.9666 | 46.9666 | 46.9666 | 46.9666 | 46.9666
03 Hydro | 42.279 | 42.279 | 37.8988 | 43.7873 | 49.7857 | 49.7857 | 49.7857 | 49.7857 | 49.7857
03 Potential Build Hydro Small | N/A | N/A | N/A | N/A | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
04 Potential Build Nuclear | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
05 Potential Build Interruptible | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
06 Potential Build Solar PV | N/A | N/A | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.0329 | 15.5867
06 Solar PV | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 17.2069
06 Potential Build Solar PV with storage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
07 Potential Build Biomass Combustion | N/A | N/A | N/A | N/A | N/A | 85 | 85 | 85 | 85
07 Potential Build Coal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
08 Potential Build Wind | N/A | N/A | N/A | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594
Average | 38.9232 | 36.3325 | 37.5532 | 40.0762 | 49.9918 | 52.9189 | 53.1415 | 50.8811 | 47.0578
(**) Ind. Boilers not included in the average
15. Total Annual Production Cost [Million US2016$](*)
Variable O&M | 42.5409 | 48.6522 | 56.9016 | 60.2875 | 74.2128 | 80.6913 | 93.4186 | 110.0705 | 128.0882
Fixed O&M | 103.6056 | 148.842 | 161.93 | 165.2202 | 171.1526 | 118.4727 | 141.3111 | 182.8247 | 236.6112
Fuel | 563.293 | 664.1962 | 940.9707 | 977.4461 | 1067.0144 | 1157.7412 | 1396.6358 | 1943.3861 | 2754.5637
Capital | 840.4565 | 1411.163 | 6.3305 | 18.0991 | 86.3254 | 185.2309 | 295.2552 | 505.972 | 776.1312
Pollutant Transport & Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1549.896 | 2272.8533 | 1166.1328 | 1221.0529 | 1398.7052 | 1542.1361 | 1926.6207 | 2742.2532 | 3895.3944
Sales Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(*) Costs include only those items that are important for determining incremental cost of pollution control (industrial boiler costs are included)
15c Annual Transmission Activity (*)
[GWh] Transmitted Out Existing Lines | 7546.3422 | 9470.8202 | 9496.1047 | 10231.4315 | 13461.7429 | 18815.8388 | 20241.6563 | 18512.5923 | 22117.0855
[GWh] Transmitted Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[MW] Transferred Out Existing Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
[MW] Transferred Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Book [MW] of Transmission Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[GWh] Transmitted Out All Lines | 7546.3422 | 9470.8202 | 9496.1047 | 10231.4315 | 13461.7429 | 18815.8388 | 20241.6563 | 18512.5923 | 22117.0855
[MW] Transferred Out All Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
16. Emissions
CO2 Thousand Tons | 5001.5616 | 5412.4114 | 7379.2588 | 7680.226 | 8841.8012 | 9160.1437 | 10871.128 | 13134.9742 | 16173.4918
NOX Thousand Tons | 28.0014 | 42.4503 | 57.8765 | 60.2371 | 69.3475 | 71.011 | 73.7597 | 67.1132 | 58.5706
SO2 Thousand Tons | 6.6656 | 0.8683 | 1.1838 | 1.2321 | 1.4185 | 1.4695 | 1.744 | 2.1072 | 2.5947
(**) Industrial Boiler emissions are included
17. Fuel Consumption by Fuel and Fuel Type [TBtu]
Fuel Type | 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
Biomass | 0.010052 | 0 | 0.010052 | 0.010052 | 0 | 6.0413 | 6.0413 | 6.0413 | 6.0413
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 47.6746 | 82.9561 | 113.102 | 117.7149 | 135.5184 | 140.3976 | 166.6219 | 201.3199 | 247.8913
Oil | 21.2622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Limited Water
Back to Contents
| 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
1. Reserve Margin Capacity Annual [MW] | 3348.7611 | 4649.4823 | 4557.3801 | 5131.924 | 5112.044 | 4790.0287 | 5296.4537 | 6338.8277 | 7814.5957
Plus Firm Contract Purchases Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Transmission In Annual [MW] | 173 | 173 | 449.625 | 509.2398 | 618.9336 | 750.2462 | 1144.926 | 1491.1568 | 2285.7662
Less Firm Contract Sales Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Transmission Out Annual [MW] | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
Total Reserve Margin Capacity Annual [MW] | 3248.7611 | 4547.4823 | 4453.3401 | 5025.803 | 4998.528 | 4608.8197 | 5024.2927 | 6009.5316 | 7464.1588
2. Peak Load Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
Less DSM [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
3. Reserve Margin Annual [%] | 52.8408 | 94.0481 | 78.466 | 87.7536 | 50.7538 | 25.281 | 17.881 | 15 | 15
3a.Local Reserves Annual [%] | 157.5454 | 198.4006 | 182.6353 | 191.7181 | 154.1774 | 130.2068 | 124.2665 | 121.3015 | 120.3992
4. Total Generation [GWh] | 13918.8433 | 15531.5324 | 17387.3067 | 17998.036 | 23370.6917 | 26198.5195 | 30668.0033 | 37352.4674 | 45790.2848
Inter-Region Transmission [GWh] | 378.6316 | 370.9514 | -441.5621 | 355.1276 | -278.1666 | -718.401 | -1320.2731 | -1622.8291 | -1679.9119
Pumping & Storage Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Purchases [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Sales [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Total Supply for Demand [GWh] | 14297.4749 | 15902.4839 | 16945.7446 | 18353.1637 | 23092.5251 | 25480.1186 | 29347.7302 | 35729.6383 | 44110.373
6. Projected Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
Energy Not Served [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less DSM [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Demand Response [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
7. Dumped Energy [GWh] | -0.00082978 | -0.0005165 | 0.0011227 | 0.0011148 | -0.00012842 | 0.00078435 | 0.0033826 | -0.02211 | 0.025502
8. Total Generation [GWh] | 13918.8433 | 15531.5324 | 17387.3067 | 17998.036 | 23370.6917 | 26198.5195 | 30668.0033 | 37352.4674 | 45790.2848
Less T&D Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9. Total Sales [GWh] | 13918.8433 | 15531.5324 | 17387.3067 | 17998.036 | 23370.6917 | 26198.5195 | 30668.0033 | 37352.4674 | 45790.2848
10. Capacity by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 524.4097 | 1636.7837 | 3112.5517
01 Oil/Gas Combined Cycle | 1492 | 2160 | 2350 | 2350 | 2350 | 1900 | 1900 | 1900 | 1900
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 455 | 504.92 | 504.92 | 504.92 | 455 | 455 | 455 | 455 | 455
02 MSW - Landfill Gas | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
02 Oil Combustion | 221 | 221 | 221 | 221 | 188.5 | 188.5 | 188.5 | 88.5 | 88.5
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 394.96 | 394.96 | 772.46 | 772.46 | 747.5 | 747.5 | 747.5 | 747.5 | 747.5
03 Hydro | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 80 | 80
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 47.1565 | 147.1565 | 347.1565 | 597.1565 | 1077.1565 | 2347.1565
06 Solar PV | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 1.8
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 145.4386 | 445.4386 | 645.4386 | 945.4386 | 945.4386
Total | 4082.161 | 4887.882 | 5285.4365 | 5355.8751 | 5503.4951 | 5651.4798 | 6587.9048 | 8380.2788 | 11108.0468
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
11. Capacity Additions and Changes by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 486.425 | 1112.374 | 1475.768
01 Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 0 | 100 | 200 | 250 | 480 | 1270
06 Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 75 | 300 | 200 | 300 | 0
Total | 129.301 | 217.102 | 47.1565 | 70.4386 | 255 | 597.9847 | 936.425 | 1892.374 | 2745.768
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
12. Generation by Capacity Reporting Type [GWh]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 299.4711 | 4134.4493 | 12904.3818 | 24539.3843
01 Oil/Gas Combined Cycle | 7999.4319 | 10430.0761 | 8713.2465 | 9188.7359 | 13724.0838 | 14604.8062 | 14617.3396 | 12383.6006 | 7538.6539
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 366.0332 | 0 | 1813.32 | 0 | 0 | 213.8722 | 574.0976 | 21.22 | 1.0391
02 MSW - Landfill Gas | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446
02 Oil Combustion | 161.4795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 290.4419 | 0 | 1291.3569 | 3075.417 | 3075.4171 | 3075.417 | 3075.417 | 3075.417 | 3075.417
03 Hydro | 5073.983 | 5073.9827 | 5474.3833 | 5474.3833 | 5740.1782 | 5740.1782 | 5176.8615 | 4519.6604 | 4519.6594
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 253.164 | 253.164 | 253.164 | 253.164 | 253.164
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 67.5263 | 67.5263 | 210.7224 | 497.1146 | 855.1048 | 1512.844 | 3204.8034
06 Solar PV | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 2.7132
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 446.76 | 446.76 | 446.76 | 446.76
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8433 | 15531.5324 | 17387.3067 | 17998.036 | 23370.6917 | 26198.5195 | 30668.0033 | 37352.4674 | 45790.2848
(**) Ind. Boiler generation in BBtu, not included in the total
12a. Generation by Fuel Type [GWh]
Biomass | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 447.5046 | 447.5046 | 447.5046 | 447.5046
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 4938.2836 | 10430.0761 | 11817.9234 | 12264.1529 | 16799.501 | 18193.5666 | 22401.3035 | 28384.6194 | 35154.4943
Oil | 3879.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 26.7291 | 26.7291 | 94.2553 | 94.2553 | 237.4514 | 523.8436 | 881.8339 | 1539.5731 | 3207.5166
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 5073.983 | 5073.9827 | 5474.3833 | 5474.3833 | 5993.3422 | 5993.3422 | 5430.0255 | 4772.8244 | 4772.8234
Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8433 | 15531.5324 | 17387.3067 | 17998.036 | 23370.6917 | 26198.5195 | 30668.0033 | 37352.4674 | 45790.2848
13. Generation by Capacity Reporting Type [TBtu]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 1.0218 | 14.1067 | 44.0298 | 83.7284
01 Oil/Gas Combined Cycle | 27.2941 | 35.5874 | 29.7296 | 31.352 | 46.8266 | 49.8316 | 49.8744 | 42.2528 | 25.7219
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 1.2489 | 0 | 6.187 | 0 | 0 | 0.72973 | 1.9588 | 0.072403 | 0.0035456
02 MSW - Landfill Gas | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406
02 Oil Combustion | 0.55097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0.99099 | 0 | 4.4061 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933
03 Hydro | 17.3124 | 17.3124 | 18.6786 | 18.6786 | 19.5855 | 19.5855 | 17.6635 | 15.4211 | 15.4211
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 0.8638 | 0.8638 | 0.8638 | 0.8638 | 0.8638
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 0.2304 | 0.2304 | 0.71898 | 1.6962 | 2.9176 | 5.1618 | 10.9348
06 Solar PV | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0092574
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 1.5243 | 1.5243 | 1.5243 | 1.5243
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 0.56127 | 1.1589 | 3.5494 | 5.143 | 7.5335 | 7.5335
Total | 47.4911 | 52.9936 | 59.3255 | 61.4093 | 79.7408 | 89.3893 | 104.6392 | 127.4466 | 156.2365
(**) Ind. Boiler generation, not included in the total
14. Capacity Factor by Capacity Reporting Type [%]
01 Potential Build Oil/Gas Combined Cycle | N/A | N/A | N/A | N/A | N/A | 89.9999 | 90.0001 | 89.9999 | 90.0001
01 Oil/Gas Combined Cycle | 61.2049 | 55.1226 | 42.3261 | 44.6358 | 66.6671 | 87.7482 | 87.8235 | 74.4028 | 45.2935
02 Potential Build Biogas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Gas Combustion Turbine | 9.1834 | 0 | 40.9966 | 0 | 0 | 5.3659 | 14.4036 | 0.53239 | 0.026071
02 MSW - Landfill Gas | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
02 Oil Combustion | 8.3411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Oil/Gas Combustion | 8.3946 | 0 | 19.0839 | 45.449 | 46.9666 | 46.9666 | 46.9666 | 46.9666 | 46.9666
03 Hydro | 42.279 | 42.279 | 45.6153 | 45.6153 | 47.83 | 47.83 | 43.1362 | 37.6601 | 37.6601
03 Potential Build Hydro Small | N/A | N/A | N/A | N/A | 36.125 | 36.125 | 36.125 | 36.125 | 36.125
04 Potential Build Nuclear | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
05 Potential Build Interruptible | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
06 Potential Build Solar PV | N/A | N/A | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.0329 | 15.5867
06 Solar PV | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 17.2069
06 Potential Build Solar PV with storage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
07 Potential Build Biomass Combustion | N/A | N/A | N/A | N/A | N/A | 85 | 85 | 85 | 85
07 Potential Build Coal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
08 Potential Build Wind | N/A | N/A | N/A | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594
Average | 38.9232 | 36.2735 | 37.5532 | 38.3611 | 48.4762 | 52.9189 | 53.1415 | 50.8811 | 47.0578
(**) Ind. Boilers not included in the average
15. Total Annual Production Cost [Million US2016$](*)
Variable O&M | 42.9388 | 48.5644 | 53.0709 | 56.0715 | 74.3146 | 81.4121 | 95.8544 | 114.6994 | 131.3594
Fixed O&M | 103.6056 | 148.842 | 161.93 | 165.2202 | 171.1526 | 118.4727 | 141.3111 | 182.8247 | 236.6112
Fuel | 586.7732 | 661.3921 | 831.0154 | 799.3597 | 1111.2275 | 1319.6662 | 1657.0255 | 2206.8923 | 2961.5557
Capital | 840.4565 | 1411.163 | 6.3305 | 18.0991 | 86.3254 | 185.2309 | 295.2552 | 505.972 | 776.1312
Pollutant Transport & Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1573.7741 | 2269.9615 | 1052.3469 | 1038.7506 | 1443.02 | 1704.782 | 2189.4462 | 3010.3884 | 4105.6576
Sales Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(*) Costs include only those items that are important for determining incremental cost of pollution control (industrial boiler costs are included)
15c Annual Transmission Activity (*)
[GWh] Transmitted Out Existing Lines | 6755.7073 | 10158.8194 | 8378.4654 | 10413.7178 | 13935.2883 | 20057.1629 | 20753.6288 | 18551.3294 | 21922.8192
[GWh] Transmitted Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[MW] Transferred Out Existing Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
[MW] Transferred Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Book [MW] of Transmission Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[GWh] Transmitted Out All Lines | 6755.7073 | 10158.8194 | 8378.4654 | 10413.7178 | 13935.2883 | 20057.1629 | 20753.6288 | 18551.3294 | 21922.8192
[MW] Transferred Out All Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
16. Emissions
CO2 Thousand Tons | 5292.4775 | 5384.369 | 6516.9423 | 6280.8797 | 8560.9128 | 9321.1872 | 11363.0849 | 13948.681 | 17003.1092
NOX Thousand Tons | 24.4837 | 42.2303 | 51.1133 | 49.2618 | 67.1444 | 72.2741 | 77.6182 | 73.4953 | 65.0774
SO2 Thousand Tons | 9.5141 | 0.8638 | 1.0455 | 1.0076 | 1.3734 | 1.4954 | 1.823 | 2.2378 | 2.7278
(**) Industrial Boiler emissions are included
17. Fuel Consumption by Fuel and Fuel Type [TBtu]
Fuel Type | 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
Biomass | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 6.0413 | 6.0413 | 6.0413 | 6.0413
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 38.2185 | 82.5263 | 99.8852 | 96.2671 | 131.2132 | 142.8659 | 174.1621 | 213.7916 | 260.6068
Oil | 31.3479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## High RECapCost
Back to Contents
| 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
1. Reserve Margin Capacity Annual [MW] | 3348.7611 | 4649.4823 | 4557.3801 | 5131.924 | 5112.044 | 4790.0287 | 5296.4537 | 6338.8277 | 7814.5957
Plus Firm Contract Purchases Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Transmission In Annual [MW] | 173 | 173 | 449.625 | 509.2398 | 618.9336 | 750.2462 | 1144.926 | 1491.1568 | 2285.7662
Less Firm Contract Sales Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Transmission Out Annual [MW] | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
Total Reserve Margin Capacity Annual [MW] | 3248.7611 | 4547.4823 | 4453.3401 | 5025.803 | 4998.528 | 4608.8197 | 5024.2927 | 6009.5316 | 7464.1588
2. Peak Load Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
Less DSM [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
3. Reserve Margin Annual [%] | 52.8408 | 94.0481 | 78.466 | 87.7536 | 50.7538 | 25.281 | 17.881 | 15 | 15
3a.Local Reserves Annual [%] | 157.5454 | 198.4006 | 182.6353 | 191.7181 | 154.1774 | 130.2068 | 124.2665 | 121.3015 | 120.3992
4. Total Generation [GWh] | 13918.8452 | 15531.5321 | 17387.3067 | 17998.0364 | 23370.6931 | 26198.5163 | 30668.0029 | 37352.4707 | 45790.2879
Inter-Region Transmission [GWh] | 378.6316 | 370.9515 | -441.5621 | 355.1277 | -278.1663 | -718.4012 | -1320.2731 | -1622.8296 | -1679.9119
Pumping & Storage Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Purchases [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Sales [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Total Supply for Demand [GWh] | 14297.4767 | 15902.4836 | 16945.7447 | 18353.1641 | 23092.5268 | 25480.1151 | 29347.7298 | 35729.6411 | 44110.376
6. Projected Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
Energy Not Served [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less DSM [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Demand Response [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
7. Dumped Energy [GWh] | 0.00099769 | -0.00079109 | 0.0011601 | 0.0015386 | 0.0015453 | -0.0026869 | 0.0029519 | -0.019247 | 0.028499
8. Total Generation [GWh] | 13918.8452 | 15531.5321 | 17387.3067 | 17998.0364 | 23370.6931 | 26198.5163 | 30668.0029 | 37352.4707 | 45790.2879
Less T&D Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9. Total Sales [GWh] | 13918.8452 | 15531.5321 | 17387.3067 | 17998.0364 | 23370.6931 | 26198.5163 | 30668.0029 | 37352.4707 | 45790.2879
10. Capacity by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 524.4097 | 1636.7837 | 3112.5517
01 Oil/Gas Combined Cycle | 1492 | 2160 | 2350 | 2350 | 2350 | 1900 | 1900 | 1900 | 1900
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 455 | 504.92 | 504.92 | 504.92 | 455 | 455 | 455 | 455 | 455
02 MSW - Landfill Gas | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
02 Oil Combustion | 221 | 221 | 221 | 221 | 188.5 | 188.5 | 188.5 | 88.5 | 88.5
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 394.96 | 394.96 | 772.46 | 772.46 | 747.5 | 747.5 | 747.5 | 747.5 | 747.5
03 Hydro | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 80 | 80
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 47.1565 | 147.1565 | 347.1565 | 597.1565 | 1077.1565 | 2347.1565
06 Solar PV | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 1.8
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 145.4386 | 445.4386 | 645.4386 | 945.4386 | 945.4386
Total | 4082.161 | 4887.882 | 5285.4365 | 5355.8751 | 5503.4951 | 5651.4798 | 6587.9048 | 8380.2788 | 11108.0468
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
11. Capacity Additions and Changes by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 486.425 | 1112.374 | 1475.768
01 Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 0 | 100 | 200 | 250 | 480 | 1270
06 Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 75 | 300 | 200 | 300 | 0
Total | 129.301 | 217.102 | 47.1565 | 70.4386 | 255 | 597.9847 | 936.425 | 1892.374 | 2745.768
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
12. Generation by Capacity Reporting Type [GWh]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 299.4711 | 4134.4496 | 12904.3845 | 24539.388
01 Oil/Gas Combined Cycle | 7999.4335 | 10430.0763 | 9015.5034 | 9188.735 | 13444.7041 | 14438.1535 | 14199.0815 | 10900.3507 | 6038.8607
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 366.0332 | 0 | 1813.32 | 0 | 0 | 101.1434 | 149.6574 | 4.5712 | 0.93205
02 MSW - Landfill Gas | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446
02 Oil Combustion | 161.4795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 290.4419 | 0 | 989.0987 | 3075.417 | 3075.4173 | 3075.417 | 3075.417 | 3075.417 | 3075.417
03 Hydro | 5073.9834 | 5073.9822 | 5474.3848 | 5474.3845 | 5974.8832 | 5974.8804 | 5974.8831 | 5974.8837 | 5974.8831
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 297.84 | 297.84 | 297.84 | 297.84 | 297.84
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 67.5263 | 67.5263 | 210.7224 | 497.1146 | 855.1048 | 1512.844 | 3204.8034
06 Solar PV | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 2.7132
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 446.76 | 446.76 | 446.76 | 446.76
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8452 | 15531.5321 | 17387.3067 | 17998.0364 | 23370.6931 | 26198.5163 | 30668.0029 | 37352.4707 | 45790.2879
(**) Ind. Boiler generation in BBtu, not included in the total
12a. Generation by Fuel Type [GWh]
Biomass | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 447.5046 | 447.5046 | 447.5046 | 447.5046
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 4938.2855 | 10430.0763 | 11817.922 | 12264.152 | 16520.1214 | 17914.1851 | 21558.6055 | 26884.7234 | 33654.5977
Oil | 3879.1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 26.7291 | 26.7291 | 94.2553 | 94.2553 | 237.4514 | 523.8436 | 881.8339 | 1539.5731 | 3207.5166
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 5073.9834 | 5073.9822 | 5474.3848 | 5474.3845 | 6272.7232 | 6272.7204 | 6272.7231 | 6272.7237 | 6272.7231
Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8452 | 15531.5321 | 17387.3067 | 17998.0364 | 23370.6931 | 26198.5163 | 30668.0029 | 37352.4707 | 45790.2879
13. Generation by Capacity Reporting Type [TBtu]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 1.0218 | 14.1067 | 44.0298 | 83.7284
01 Oil/Gas Combined Cycle | 27.2941 | 35.5874 | 30.7609 | 31.352 | 45.8733 | 49.263 | 48.4473 | 37.192 | 20.6046
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 1.2489 | 0 | 6.187 | 0 | 0 | 0.3451 | 0.51063 | 0.015597 | 0.0031802
02 MSW - Landfill Gas | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406
02 Oil Combustion | 0.55097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0.99099 | 0 | 3.3748 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933
03 Hydro | 17.3124 | 17.3124 | 18.6786 | 18.6786 | 20.3863 | 20.3863 | 20.3863 | 20.3863 | 20.3863
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 1.0162
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 0.2304 | 0.2304 | 0.71898 | 1.6962 | 2.9176 | 5.1618 | 10.9348
06 Solar PV | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0092574
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 1.5243 | 1.5243 | 1.5243 | 1.5243
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 0.56127 | 1.1589 | 3.5494 | 5.143 | 7.5335 | 7.5335
Total | 47.4911 | 52.9936 | 59.3255 | 61.4093 | 79.7408 | 89.3893 | 104.6392 | 127.4466 | 156.2365
(**) Ind. Boiler generation, not included in the total
14. Capacity Factor by Capacity Reporting Type [%]
01 Potential Build Oil/Gas Combined Cycle | N/A | N/A | N/A | N/A | N/A | 89.9999 | 90.0001 | 89.9999 | 90.0001
01 Oil/Gas Combined Cycle | 61.2049 | 55.1226 | 43.7943 | 44.6358 | 65.3099 | 86.7469 | 85.3105 | 65.4912 | 36.2825
02 Potential Build Biogas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Gas Combustion Turbine | 9.1834 | 0 | 40.9966 | 0 | 0 | 2.5376 | 3.7548 | 0.11469 | 0.023384
02 MSW - Landfill Gas | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
02 Oil Combustion | 8.3411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Oil/Gas Combustion | 8.3946 | 0 | 14.617 | 45.449 | 46.9666 | 46.9666 | 46.9666 | 46.9666 | 46.9666
03 Hydro | 42.279 | 42.279 | 45.6153 | 45.6153 | 49.7857 | 49.7857 | 49.7857 | 49.7857 | 49.7857
03 Potential Build Hydro Small | N/A | N/A | N/A | N/A | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
04 Potential Build Nuclear | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
05 Potential Build Interruptible | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
06 Potential Build Solar PV | N/A | N/A | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.0329 | 15.5867
06 Solar PV | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 17.2069
06 Potential Build Solar PV with storage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
07 Potential Build Biomass Combustion | N/A | N/A | N/A | N/A | N/A | 85 | 85 | 85 | 85
07 Potential Build Coal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
08 Potential Build Wind | N/A | N/A | N/A | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594
Average | 38.9232 | 36.2735 | 37.5532 | 38.3611 | 48.4762 | 52.9189 | 53.1415 | 50.8811 | 47.0578
(**) Ind. Boilers not included in the average
15. Total Annual Production Cost [Million US2016$](*)
Variable O&M | 42.9388 | 48.5644 | 53.0709 | 56.0715 | 73.7065 | 80.6913 | 93.4186 | 110.0705 | 127.6875
Fixed O&M | 103.6056 | 148.842 | 161.93 | 165.2202 | 171.1526 | 118.4727 | 141.3111 | 182.8247 | 236.6112
Fuel | 586.7733 | 661.3921 | 831.0153 | 799.3597 | 1086.8288 | 1293.4165 | 1578.0739 | 2070.6596 | 2798.3246
Capital | 840.4565 | 1411.163 | 6.3305 | 20.6095 | 102.8405 | 220.1001 | 340.1661 | 574.3931 | 880.2139
Pollutant Transport & Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1573.7741 | 2269.9615 | 1052.3468 | 1041.2609 | 1434.5283 | 1712.6806 | 2152.9697 | 2937.9478 | 4042.8373
Sales Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(*) Costs include only those items that are important for determining incremental cost of pollution control (industrial boiler costs are included)
15c Annual Transmission Activity (*)
[GWh] Transmitted Out Existing Lines | 6426.4326 | 9423.1453 | 7568.5132 | 10987.5053 | 15388.1412 | 19989.2919 | 19698.2149 | 19074.7124 | 22138.5732
[GWh] Transmitted Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[MW] Transferred Out Existing Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
[MW] Transferred Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Book [MW] of Transmission Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[GWh] Transmitted Out All Lines | 6426.4326 | 9423.1453 | 7568.5132 | 10987.5053 | 15388.1412 | 19989.2919 | 19698.2149 | 19074.7124 | 22138.5732
[MW] Transferred Out All Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
16. Emissions
CO2 Thousand Tons | 5292.4781 | 5384.3691 | 6516.9416 | 6280.8792 | 8405.9755 | 9160.1442 | 10871.1282 | 13134.9739 | 16186.7816
NOX Thousand Tons | 24.4838 | 42.2303 | 51.1133 | 49.2618 | 65.9292 | 71.011 | 73.7597 | 67.1132 | 58.6749
SO2 Thousand Tons | 9.5141 | 0.8638 | 1.0455 | 1.0076 | 1.3486 | 1.4695 | 1.744 | 2.1072 | 2.5968
(**) Industrial Boiler emissions are included
17. Fuel Consumption by Fuel and Fuel Type [TBtu]
Fuel Type | 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
Biomass | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 6.0413 | 6.0413 | 6.0413 | 6.0413
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 38.2185 | 82.5263 | 99.8852 | 96.2671 | 128.8385 | 140.3976 | 166.6219 | 201.3199 | 248.095
Oil | 31.3479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LowRECapCost
Back to Contents
| 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
1. Reserve Margin Capacity Annual [MW] | 3348.7611 | 4649.4823 | 4557.3801 | 5131.924 | 5112.044 | 4790.0287 | 5296.4537 | 6338.8277 | 7814.5957
Plus Firm Contract Purchases Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Transmission In Annual [MW] | 173 | 173 | 449.625 | 509.2398 | 618.9336 | 750.2462 | 1144.926 | 1491.1568 | 2285.7662
Less Firm Contract Sales Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Transmission Out Annual [MW] | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
Total Reserve Margin Capacity Annual [MW] | 3248.7611 | 4547.4823 | 4453.3401 | 5025.803 | 4998.528 | 4608.8197 | 5024.2927 | 6009.5316 | 7464.1588
2. Peak Load Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
Less DSM [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
3. Reserve Margin Annual [%] | 52.8408 | 94.0481 | 78.466 | 87.7536 | 50.7538 | 25.281 | 17.881 | 15 | 15
3a.Local Reserves Annual [%] | 157.5454 | 198.4006 | 182.6353 | 191.7181 | 154.1774 | 130.2068 | 124.2665 | 121.3015 | 120.3992
4. Total Generation [GWh] | 13918.8452 | 15531.5321 | 17387.3067 | 17998.0364 | 23370.6931 | 26198.5163 | 30668.0029 | 37352.4707 | 45790.2879
Inter-Region Transmission [GWh] | 378.6316 | 370.9515 | -441.5621 | 355.1277 | -278.1663 | -718.4012 | -1320.2731 | -1622.8296 | -1679.9119
Pumping & Storage Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Purchases [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Sales [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Total Supply for Demand [GWh] | 14297.4767 | 15902.4836 | 16945.7447 | 18353.1641 | 23092.5268 | 25480.1151 | 29347.7298 | 35729.6411 | 44110.376
6. Projected Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
Energy Not Served [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less DSM [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Demand Response [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
7. Dumped Energy [GWh] | 0.00099769 | -0.00079109 | 0.0011601 | 0.0015386 | 0.0015453 | -0.0026869 | 0.0029519 | -0.019247 | 0.028499
8. Total Generation [GWh] | 13918.8452 | 15531.5321 | 17387.3067 | 17998.0364 | 23370.6931 | 26198.5163 | 30668.0029 | 37352.4707 | 45790.2879
Less T&D Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9. Total Sales [GWh] | 13918.8452 | 15531.5321 | 17387.3067 | 17998.0364 | 23370.6931 | 26198.5163 | 30668.0029 | 37352.4707 | 45790.2879
10. Capacity by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 524.4097 | 1636.7837 | 3112.5517
01 Oil/Gas Combined Cycle | 1492 | 2160 | 2350 | 2350 | 2350 | 1900 | 1900 | 1900 | 1900
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 455 | 504.92 | 504.92 | 504.92 | 455 | 455 | 455 | 455 | 455
02 MSW - Landfill Gas | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
02 Oil Combustion | 221 | 221 | 221 | 221 | 188.5 | 188.5 | 188.5 | 88.5 | 88.5
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 394.96 | 394.96 | 772.46 | 772.46 | 747.5 | 747.5 | 747.5 | 747.5 | 747.5
03 Hydro | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 80 | 80
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 47.1565 | 147.1565 | 347.1565 | 597.1565 | 1077.1565 | 2347.1565
06 Solar PV | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 1.8
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 145.4386 | 445.4386 | 645.4386 | 945.4386 | 945.4386
Total | 4082.161 | 4887.882 | 5285.4365 | 5355.8751 | 5503.4951 | 5651.4798 | 6587.9048 | 8380.2788 | 11108.0468
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
11. Capacity Additions and Changes by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 486.425 | 1112.374 | 1475.768
01 Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 0 | 100 | 200 | 250 | 480 | 1270
06 Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 75 | 300 | 200 | 300 | 0
Total | 129.301 | 217.102 | 47.1565 | 70.4386 | 255 | 597.9847 | 936.425 | 1892.374 | 2745.768
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
12. Generation by Capacity Reporting Type [GWh]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 299.4711 | 4134.4496 | 12904.3845 | 24539.388
01 Oil/Gas Combined Cycle | 7999.4335 | 10430.0763 | 9015.5034 | 9188.735 | 13444.7041 | 14438.1535 | 14199.0815 | 10900.3507 | 6038.8607
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 366.0332 | 0 | 1813.32 | 0 | 0 | 101.1434 | 149.6574 | 4.5712 | 0.93205
02 MSW - Landfill Gas | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446
02 Oil Combustion | 161.4795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 290.4419 | 0 | 989.0987 | 3075.417 | 3075.4173 | 3075.417 | 3075.417 | 3075.417 | 3075.417
03 Hydro | 5073.9834 | 5073.9822 | 5474.3848 | 5474.3845 | 5974.8832 | 5974.8804 | 5974.8831 | 5974.8837 | 5974.8831
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 297.84 | 297.84 | 297.84 | 297.84 | 297.84
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 67.5263 | 67.5263 | 210.7224 | 497.1146 | 855.1048 | 1512.844 | 3204.8034
06 Solar PV | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 2.7132
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 446.76 | 446.76 | 446.76 | 446.76
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8452 | 15531.5321 | 17387.3067 | 17998.0364 | 23370.6931 | 26198.5163 | 30668.0029 | 37352.4707 | 45790.2879
(**) Ind. Boiler generation in BBtu, not included in the total
12a. Generation by Fuel Type [GWh]
Biomass | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 447.5046 | 447.5046 | 447.5046 | 447.5046
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 4938.2855 | 10430.0763 | 11817.922 | 12264.152 | 16520.1214 | 17914.1851 | 21558.6055 | 26884.7234 | 33654.5977
Oil | 3879.1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 26.7291 | 26.7291 | 94.2553 | 94.2553 | 237.4514 | 523.8436 | 881.8339 | 1539.5731 | 3207.5166
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 5073.9834 | 5073.9822 | 5474.3848 | 5474.3845 | 6272.7232 | 6272.7204 | 6272.7231 | 6272.7237 | 6272.7231
Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8452 | 15531.5321 | 17387.3067 | 17998.0364 | 23370.6931 | 26198.5163 | 30668.0029 | 37352.4707 | 45790.2879
13. Generation by Capacity Reporting Type [TBtu]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 1.0218 | 14.1067 | 44.0298 | 83.7284
01 Oil/Gas Combined Cycle | 27.2941 | 35.5874 | 30.7609 | 31.352 | 45.8733 | 49.263 | 48.4473 | 37.192 | 20.6046
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 1.2489 | 0 | 6.187 | 0 | 0 | 0.3451 | 0.51063 | 0.015597 | 0.0031802
02 MSW - Landfill Gas | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406
02 Oil Combustion | 0.55097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0.99099 | 0 | 3.3748 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933
03 Hydro | 17.3124 | 17.3124 | 18.6786 | 18.6786 | 20.3863 | 20.3863 | 20.3863 | 20.3863 | 20.3863
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 1.0162
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 0.2304 | 0.2304 | 0.71898 | 1.6962 | 2.9176 | 5.1618 | 10.9348
06 Solar PV | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0092574
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 1.5243 | 1.5243 | 1.5243 | 1.5243
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 0.56127 | 1.1589 | 3.5494 | 5.143 | 7.5335 | 7.5335
Total | 47.4911 | 52.9936 | 59.3255 | 61.4093 | 79.7408 | 89.3893 | 104.6392 | 127.4466 | 156.2365
(**) Ind. Boiler generation, not included in the total
14. Capacity Factor by Capacity Reporting Type [%]
01 Potential Build Oil/Gas Combined Cycle | N/A | N/A | N/A | N/A | N/A | 89.9999 | 90.0001 | 89.9999 | 90.0001
01 Oil/Gas Combined Cycle | 61.2049 | 55.1226 | 43.7943 | 44.6358 | 65.3099 | 86.7469 | 85.3105 | 65.4912 | 36.2825
02 Potential Build Biogas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Gas Combustion Turbine | 9.1834 | 0 | 40.9966 | 0 | 0 | 2.5376 | 3.7548 | 0.11469 | 0.023384
02 MSW - Landfill Gas | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
02 Oil Combustion | 8.3411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Oil/Gas Combustion | 8.3946 | 0 | 14.617 | 45.449 | 46.9666 | 46.9666 | 46.9666 | 46.9666 | 46.9666
03 Hydro | 42.279 | 42.279 | 45.6153 | 45.6153 | 49.7857 | 49.7857 | 49.7857 | 49.7857 | 49.7857
03 Potential Build Hydro Small | N/A | N/A | N/A | N/A | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
04 Potential Build Nuclear | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
05 Potential Build Interruptible | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
06 Potential Build Solar PV | N/A | N/A | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.0329 | 15.5867
06 Solar PV | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 17.2069
06 Potential Build Solar PV with storage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
07 Potential Build Biomass Combustion | N/A | N/A | N/A | N/A | N/A | 85 | 85 | 85 | 85
07 Potential Build Coal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
08 Potential Build Wind | N/A | N/A | N/A | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594
Average | 38.9232 | 36.2735 | 37.5532 | 38.3611 | 48.4762 | 52.9189 | 53.1415 | 50.8811 | 47.0578
(**) Ind. Boilers not included in the average
15. Total Annual Production Cost [Million US2016$](*)
Variable O&M | 42.9388 | 48.5644 | 53.0709 | 56.0715 | 73.7065 | 80.6913 | 93.4186 | 110.0705 | 127.6875
Fixed O&M | 103.6056 | 148.842 | 161.93 | 165.2202 | 171.1526 | 118.4727 | 141.3111 | 182.8247 | 236.6112
Fuel | 586.7733 | 661.3921 | 831.0153 | 799.3597 | 1086.8288 | 1293.4165 | 1578.0739 | 2070.6596 | 2798.3246
Capital | 840.4565 | 1411.163 | 6.3305 | 13.7096 | 67.0012 | 139.1056 | 233.2647 | 419.092 | 668.3792
Pollutant Transport & Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1573.7741 | 2269.9615 | 1052.3468 | 1034.361 | 1398.689 | 1631.6861 | 2046.0683 | 2782.6467 | 3831.0025
Sales Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(*) Costs include only those items that are important for determining incremental cost of pollution control (industrial boiler costs are included)
15c Annual Transmission Activity (*)
[GWh] Transmitted Out Existing Lines | 6426.4326 | 9423.1453 | 7568.5132 | 10987.5053 | 15388.1412 | 19989.2919 | 19698.2149 | 19074.7124 | 22138.5732
[GWh] Transmitted Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[MW] Transferred Out Existing Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
[MW] Transferred Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Book [MW] of Transmission Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[GWh] Transmitted Out All Lines | 6426.4326 | 9423.1453 | 7568.5132 | 10987.5053 | 15388.1412 | 19989.2919 | 19698.2149 | 19074.7124 | 22138.5732
[MW] Transferred Out All Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
16. Emissions
CO2 Thousand Tons | 5292.4781 | 5384.3691 | 6516.9416 | 6280.8792 | 8405.9755 | 9160.1442 | 10871.1282 | 13134.9739 | 16186.7816
NOX Thousand Tons | 24.4838 | 42.2303 | 51.1133 | 49.2618 | 65.9292 | 71.011 | 73.7597 | 67.1132 | 58.6749
SO2 Thousand Tons | 9.5141 | 0.8638 | 1.0455 | 1.0076 | 1.3486 | 1.4695 | 1.744 | 2.1072 | 2.5968
(**) Industrial Boiler emissions are included
17. Fuel Consumption by Fuel and Fuel Type [TBtu]
Fuel Type | 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
Biomass | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 6.0413 | 6.0413 | 6.0413 | 6.0413
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 38.2185 | 82.5263 | 99.8852 | 96.2671 | 128.8385 | 140.3976 | 166.6219 | 201.3199 | 248.095
Oil | 31.3479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## HighDemandHighCostLowWater
Back to Contents
| 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
1. Reserve Margin Capacity Annual [MW] | 3348.7611 | 4653.8273 | 4557.3801 | 5167.4216 | 5302.5466 | 5237.1747 | 6937.1295 | 10307.4495 | 12725.8295
Plus Firm Contract Purchases Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Transmission In Annual [MW] | 173 | 173 | 564.5049 | 613.7685 | 588.5962 | 533.552 | 1883.587 | 4281.769 | 5507.597
Less Firm Contract Sales Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Transmission Out Annual [MW] | 273 | 275 | 668.5449 | 719.8895 | 701.2122 | 571.9696 | 2155.748 | 4611.494 | 5857.987
Total Reserve Margin Capacity Annual [MW] | 3248.7611 | 4551.8273 | 4453.3401 | 5061.3006 | 5189.9306 | 5198.7571 | 6664.9685 | 9977.7245 | 12375.4395
2. Peak Load Annual [MW] | 2125.5848 | 2496.43 | 3024.9083 | 3323.7371 | 3872.3344 | 4520.6582 | 5669.413 | 7792.2804 | 10761.2471
Less DSM [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand Annual [MW] | 2125.5848 | 2496.43 | 3024.9083 | 3323.7371 | 3872.3344 | 4520.6582 | 5669.413 | 7792.2804 | 10761.2471
3. Reserve Margin Annual [%] | 52.8408 | 82.3335 | 47.2223 | 52.2774 | 34.0259 | 15 | 17.5601 | 28.0463 | 15
3a.Local Reserves Annual [%] | 157.5454 | 186.4193 | 150.6618 | 155.4702 | 136.9341 | 115.8498 | 122.3606 | 132.2777 | 118.2561
4. Total Generation [GWh] | 13918.8432 | 16638.3267 | 20248.74 | 22897.7037 | 27150.9534 | 31862.0913 | 40083.9221 | 54469.7308 | 74225.0139
Inter-Region Transmission [GWh] | 378.6318 | 370.9514 | 363.1179 | 355.1277 | -278.1667 | -718.4012 | -1320.2728 | -1622.8298 | -1679.9116
Pumping & Storage Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Purchases [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Sales [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Total Supply for Demand [GWh] | 14297.475 | 17009.2781 | 20611.8578 | 23252.8314 | 26872.7867 | 31143.6901 | 38763.6493 | 52846.901 | 72545.1023
6. Projected Demand [GWh] | 14297.4757 | 17009.2791 | 20611.8585 | 23252.831 | 26872.7864 | 31143.6908 | 38763.6498 | 52846.908 | 72545.1116
Energy Not Served [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less DSM [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Demand Response [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand [GWh] | 14297.4757 | 17009.2791 | 20611.8585 | 23252.831 | 26872.7864 | 31143.6908 | 38763.6498 | 52846.908 | 72545.1116
7. Dumped Energy [GWh] | -0.00072992 | -0.00095869 | -0.00071295 | 0.00034539 | 0.00028043 | -0.00065995 | -0.00043976 | -0.0069811 | -0.0092425
8. Total Generation [GWh] | 13918.8432 | 16638.3267 | 20248.74 | 22897.7037 | 27150.9534 | 31862.0913 | 40083.9221 | 54469.7308 | 74225.0139
Less T&D Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9. Total Sales [GWh] | 13918.8432 | 16638.3267 | 20248.74 | 22897.7037 | 27150.9534 | 31862.0913 | 40083.9221 | 54469.7308 | 74225.0139
10. Capacity by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 965.0855 | 965.0855 | 3200.4655
01 Oil/Gas Combined Cycle | 1492 | 2160 | 2350 | 2350 | 2350 | 1900 | 1900 | 1900 | 1900
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 455 | 504.92 | 504.92 | 504.92 | 455 | 455 | 455 | 455 | 455
02 MSW - Landfill Gas | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
02 Oil Combustion | 221 | 221 | 221 | 221 | 188.5 | 188.5 | 188.5 | 88.5 | 88.5
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 394.96 | 394.96 | 772.46 | 772.46 | 747.5 | 747.5 | 747.5 | 747.5 | 747.5
03 Hydro | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 80 | 80
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4640.32 | 4640.32
05 Potential Build Interruptible | 129.301 | 221.447 | 0 | 35.4976 | 190.5026 | 447.146 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 47.1565 | 147.1565 | 347.1565 | 1137.1565 | 1437.1565 | 2707.1565
06 Solar PV | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 1.8
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 145.4386 | 445.4386 | 645.4386 | 945.4386 | 945.4386
Total | 4082.161 | 4892.227 | 5285.4365 | 5391.3727 | 5693.9977 | 6098.6258 | 8768.5806 | 12708.9006 | 16806.2806
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
11. Capacity Additions and Changes by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 927.1008 | 0 | 2235.38
01 Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 3440.32 | 0
05 Potential Build Interruptible | 129.301 | 221.447 | 0 | 35.4976 | 190.5026 | 447.146 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 0 | 100 | 200 | 790 | 300 | 1270
06 Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 75 | 300 | 200 | 300 | 0
Total | 129.301 | 221.447 | 47.1565 | 105.9362 | 445.5026 | 1045.1307 | 3117.1008 | 4040.32 | 4115.38
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
12. Generation by Capacity Reporting Type [GWh]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 299.4711 | 7608.7345 | 4760.3915 | 22175.0067
01 Oil/Gas Combined Cycle | 7999.4327 | 11536.8706 | 13651.4096 | 14088.4031 | 17504.3456 | 14894.9701 | 10462.2177 | 1582.6509 | 574.5169
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 109.4182 | 0 | 0 | 0 | 0 | 3604.48 | 0 | 0 | 0
02 MSW - Landfill Gas | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.72709 | 0.7446
02 Oil Combustion | 161.4795 | 0 | 0 | 0 | 0 | 718.1303 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 547.0568 | 0 | 1027.9476 | 3075.417 | 3075.417 | 4340.0873 | 3075.417 | 119.504 | 993.5116
03 Hydro | 5073.9823 | 5073.9824 | 5474.3828 | 5474.3837 | 5740.1782 | 5740.1778 | 5176.8618 | 4519.66 | 4519.6599
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 253.164 | 253.164 | 253.164 | 253.164 | 253.164
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 9986.4 | 38602.8251 | 38616.708
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 67.5263 | 67.5263 | 210.7224 | 497.1146 | 1539.5575 | 1969.1458 | 3661.1052
06 Solar PV | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 2.7132
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773.178
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 446.76 | 446.76 | 426.9874 | 446.76
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8432 | 16638.3267 | 20248.74 | 22897.7037 | 27150.9534 | 31862.0913 | 40083.9221 | 54469.7308 | 74225.0139
(**) Ind. Boiler generation in BBtu, not included in the total
12a. Generation by Fuel Type [GWh]
Biomass | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 447.5046 | 447.5046 | 427.7145 | 447.5046
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 4672.1155 | 9953.6781 | 11093.6202 | 11317.8176 | 11184.4521 | 8286.331 | 9085.408 | 6462.5465 | 2065.9543
Oil | 4145.2716 | 1583.1925 | 3585.7371 | 5846.0025 | 9395.3105 | 15570.8078 | 12060.9613 | 0 | 21677.0809
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 26.7291 | 26.7291 | 94.2553 | 94.2553 | 237.4514 | 523.8436 | 1566.2866 | 1995.8749 | 4436.9964
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 9986.4 | 38602.8251 | 38616.708
Water | 5073.9823 | 5073.9824 | 5474.3828 | 5474.3837 | 5993.3422 | 5993.3418 | 5430.0258 | 4772.824 | 4772.8239
Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8432 | 16638.3267 | 20248.74 | 22897.7037 | 27150.9534 | 31862.0913 | 40083.9221 | 54469.7308 | 74225.0139
13. Generation by Capacity Reporting Type [TBtu]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 1.0218 | 25.961 | 16.2425 | 75.6611
01 Oil/Gas Combined Cycle | 27.2941 | 39.3638 | 46.5786 | 48.0696 | 59.7248 | 50.8216 | 35.6971 | 5.4 | 1.9603
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0.37333 | 0 | 0 | 0 | 0 | 12.2985 | 0 | 0 | 0
02 MSW - Landfill Gas | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0024808 | 0.0025406
02 Oil Combustion | 0.55097 | 0 | 0 | 0 | 0 | 2.4503 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 1.8666 | 0 | 3.5074 | 10.4933 | 10.4933 | 14.8084 | 10.4933 | 0.40775 | 3.3899
03 Hydro | 17.3124 | 17.3124 | 18.6786 | 18.6786 | 19.5855 | 19.5855 | 17.6635 | 15.4211 | 15.4211
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 0.8638 | 0.8638 | 0.8638 | 0.8638 | 0.8638
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 34.0736 | 131.7128 | 131.7602
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 0.2304 | 0.2304 | 0.71898 | 1.6962 | 5.253 | 6.7187 | 12.4917
06 Solar PV | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0092574
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6381
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 1.5243 | 1.5243 | 1.4569 | 1.5243
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 0.56127 | 1.1589 | 3.5494 | 5.143 | 7.5335 | 7.5335
Total | 47.4911 | 56.77 | 69.0887 | 78.127 | 92.6391 | 108.7135 | 136.7663 | 185.8507 | 253.2557
(**) Ind. Boiler generation, not included in the total
14. Capacity Factor by Capacity Reporting Type [%]
01 Potential Build Oil/Gas Combined Cycle | N/A | N/A | N/A | N/A | N/A | 89.9999 | 90 | 56.3083 | 79.0945
01 Oil/Gas Combined Cycle | 61.2049 | 60.972 | 66.314 | 68.4368 | 85.0303 | 89.4915 | 62.8588 | 9.5088 | 3.4518
02 Potential Build Biogas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Gas Combustion Turbine | 2.7452 | 0 | 0 | 0 | 0 | 90.433 | 0 | 0 | 0
02 MSW - Landfill Gas | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 83.0011 | 85
02 Oil Combustion | 8.3411 | 0 | 0 | 0 | 0 | 43.4898 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Oil/Gas Combustion | 15.8116 | 0 | 15.1912 | 45.449 | 46.9666 | 66.2801 | 46.9666 | 1.825 | 15.1725
03 Hydro | 42.279 | 42.279 | 45.6153 | 45.6153 | 47.83 | 47.83 | 43.1362 | 37.6601 | 37.6601
03 Potential Build Hydro Small | N/A | N/A | N/A | N/A | 36.125 | 36.125 | 36.125 | 36.125 | 36.125
04 Potential Build Nuclear | N/A | N/A | N/A | N/A | N/A | N/A | 95 | 94.9658 | 94.9999
05 Potential Build Interruptible | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A
06 Potential Build Solar PV | N/A | N/A | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 15.4551 | 15.6412 | 15.4381
06 Solar PV | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 17.2069
06 Potential Build Solar PV with storage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 14.4692
07 Potential Build Biomass Combustion | N/A | N/A | N/A | N/A | N/A | 85 | 85 | 81.2381 | 85
07 Potential Build Coal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
08 Potential Build Wind | N/A | N/A | N/A | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594
Average | 38.9232 | 38.8239 | 43.7334 | 48.4829 | 54.4332 | 59.6401 | 52.1839 | 48.9264 | 50.4167
(**) Ind. Boilers not included in the average
15. Total Annual Production Cost [Million US2016$](*)
Variable O&M | 42.6822 | 52.4382 | 65.2113 | 74.5754 | 86.089 | 104.4573 | 110.6279 | 121.04 | 179.4393
Fixed O&M | 103.6056 | 148.842 | 161.93 | 165.2202 | 171.1526 | 118.4727 | 281.3132 | 645.6732 | 727.9339
Fuel | 600.6946 | 767.04 | 1083.9672 | 1399.8109 | 1914.8993 | 2930.1412 | 2307.9672 | 928.0771 | 3531.4945
Capital | 840.4565 | 1439.4055 | 6.3305 | 251.3439 | 102.8405 | 220.1001 | 1256.9936 | 3662.2294 | 4135.3778
Pollutant Transport & Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1587.4389 | 2407.7256 | 1317.439 | 1890.9504 | 2274.9813 | 3373.1714 | 3956.9019 | 5357.0197 | 8574.2457
Sales Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(*) Costs include only those items that are important for determining incremental cost of pollution control (industrial boiler costs are included)
15c Annual Transmission Activity (*)
[GWh] Transmitted Out Existing Lines | 5597.3128 | 12591.8306 | 15308.8643 | 16368.8912 | 17999.6082 | 20965.603 | 23567.2986 | 26595.4964 | 33693.2247
[GWh] Transmitted Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 550.5026 | 22297.8712 | 18381.4864
[MW] Transferred Out Existing Lines | 273 | 275 | 668.5449 | 719.8895 | 701.2122 | 571.9696 | 1575.454 | 1817.784 | 2636.295
[MW] Transferred Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 580.294 | 2793.71 | 3221.692
Book [MW] of Transmission Builds | 0 | 0 | 0 | 0 | 0 | 0 | 580.294 | 2793.71 | 3221.692
[GWh] Transmitted Out All Lines | 5597.3128 | 12591.8306 | 15308.8643 | 16368.8912 | 17999.6082 | 20965.603 | 24117.8012 | 48893.3676 | 52074.7111
[MW] Transferred Out All Lines | 273 | 275 | 668.5449 | 719.8895 | 701.2122 | 571.9696 | 2155.748 | 4611.494 | 5857.987
16. Emissions
CO2 Thousand Tons | 5387.1032 | 6310.4036 | 8383.7551 | 10177.5671 | 12420.5889 | 15506.6685 | 12435.3346 | 3079.0376 | 13583.8374
NOX Thousand Tons | 23.5331 | 42.0148 | 48.8226 | 52.2289 | 53.6233 | 58.0067 | 39.7057 | 10.9036 | 4.5275
SO2 Thousand Tons | 10.1178 | 5.3639 | 11.1973 | 17.6894 | 20.7725 | 18.6641 | 23.2853 | 0.49396 | 0.16001
(**) Industrial Boiler emissions are included
17. Fuel Consumption by Fuel and Fuel Type [TBtu]
Fuel Type | 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
Biomass | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 6.0413 | 6.0413 | 5.7741 | 6.0413
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 35.8097 | 78.1225 | 86.3919 | 87.3702 | 86.4326 | 75.7458 | 70.0604 | 47.1924 | 15.2872
Oil | 34.145 | 13.4793 | 30.5187 | 49.7373 | 77.3412 | 124.2381 | 89.9318 | 0 | 157.3304
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 102.8599 | 397.6091 | 397.7521
Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LowDemandHighCostLowWater
Back to Contents
| 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
1. Reserve Margin Capacity Annual [MW] | 3348.7611 | 4645.1333 | 4557.3801 | 5131.924 | 5112.044 | 4790.0287 | 5010.8017 | 5508.1857 | 5831.3047
Plus Firm Contract Purchases Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Transmission In Annual [MW] | 173 | 173 | 387.8266 | 388.6985 | 435.8945 | 459.7116 | 609.4964 | 755.121 | 791.172
Less Firm Contract Sales Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Transmission Out Annual [MW] | 273 | 275 | 491.8666 | 494.8195 | 549.4105 | 640.9206 | 881.6574 | 1084.846 | 1142.062
Total Reserve Margin Capacity Annual [MW] | 3248.7611 | 4543.1333 | 4453.3401 | 5025.803 | 4998.528 | 4608.8197 | 4738.6407 | 5178.4607 | 5480.4147
2. Peak Load Annual [MW] | 2125.5848 | 2290.5298 | 2260.368 | 2238.3094 | 2385.5284 | 2532.6385 | 2747.435 | 3075.7252 | 3434.4983
Less DSM [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand Annual [MW] | 2125.5848 | 2290.5298 | 2260.368 | 2238.3094 | 2385.5284 | 2532.6385 | 2747.435 | 3075.7252 | 3434.4983
3. Reserve Margin Annual [%] | 52.8408 | 98.3442 | 97.0184 | 124.5357 | 109.5355 | 81.977 | 72.4751 | 68.3655 | 59.5696
3a.Local Reserves Annual [%] | 157.5454 | 202.7973 | 201.6212 | 229.2768 | 214.294 | 189.132 | 182.3811 | 179.0858 | 169.7862
4. Total Generation [GWh] | 13918.8432 | 15167.4253 | 14956.3348 | 14827.1547 | 16428.9907 | 17833.0796 | 19856.2028 | 22331.8093 | 24762.4357
Inter-Region Transmission [GWh] | 378.6314 | 370.9515 | 363.118 | 355.1275 | -278.1665 | -718.4013 | -1320.273 | -1623.3854 | -1680.4398
Pumping & Storage Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Purchases [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Sales [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Total Supply for Demand [GWh] | 14297.4747 | 15538.3768 | 15319.4528 | 15182.2822 | 16150.8241 | 17114.6784 | 18535.9298 | 20708.4239 | 23081.9959
6. Projected Demand [GWh] | 14297.4757 | 15538.3766 | 15319.4508 | 15182.2806 | 16150.8245 | 17114.6789 | 18535.9261 | 20708.4266 | 23081.9991
Energy Not Served [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less DSM [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Demand Response [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand [GWh] | 14297.4757 | 15538.3766 | 15319.4508 | 15182.2806 | 16150.8245 | 17114.6789 | 18535.9261 | 20708.4266 | 23081.9991
7. Dumped Energy [GWh] | -0.0010773 | 0.00018485 | 0.0019377 | 0.0015978 | -0.00037424 | -0.00056175 | 0.0037238 | -0.0027987 | -0.0032255
8. Total Generation [GWh] | 13918.8432 | 15167.4253 | 14956.3348 | 14827.1547 | 16428.9907 | 17833.0796 | 19856.2028 | 22331.8093 | 24762.4357
Less T&D Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9. Total Sales [GWh] | 13918.8432 | 15167.4253 | 14956.3348 | 14827.1547 | 16428.9907 | 17833.0796 | 19856.2028 | 22331.8093 | 24762.4357
10. Capacity by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 37.9847 | 37.9847 | 178.1037
01 Oil/Gas Combined Cycle | 1492 | 2160 | 2350 | 2350 | 2350 | 1900 | 1900 | 1900 | 1900
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 455 | 504.92 | 504.92 | 504.92 | 455 | 455 | 455 | 455 | 455
02 MSW - Landfill Gas | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
02 Oil Combustion | 221 | 221 | 221 | 221 | 188.5 | 188.5 | 188.5 | 88.5 | 88.5
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 394.96 | 394.96 | 772.46 | 772.46 | 747.5 | 747.5 | 747.5 | 747.5 | 747.5
03 Hydro | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 80 | 80
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 200.773 | 768.157 | 768.157
05 Potential Build Interruptible | 129.301 | 212.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 47.1565 | 147.1565 | 347.1565 | 1137.1565 | 1617.1565 | 2887.1565
06 Solar PV | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 1.8
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 145.4386 | 445.4386 | 645.4386 | 945.4386 | 945.4386
Total | 4082.161 | 4883.533 | 5285.4365 | 5355.8751 | 5503.4951 | 5651.4798 | 6842.2528 | 8089.6368 | 10091.7558
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
11. Capacity Additions and Changes by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 0 | 0 | 140.119
01 Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 200.773 | 567.384 | 0
05 Potential Build Interruptible | 129.301 | 212.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 0 | 100 | 200 | 790 | 480 | 1270
06 Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 75 | 300 | 200 | 300 | 0
Total | 129.301 | 212.753 | 47.1565 | 70.4386 | 255 | 597.9847 | 1190.773 | 1347.384 | 2020.119
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
12. Generation by Capacity Reporting Type [GWh]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 299.4711 | 299.4711 | 299.4711 | 1404.1684
01 Oil/Gas Combined Cycle | 7999.4309 | 10065.9691 | 8359.0027 | 6017.8536 | 6782.3838 | 6587.553 | 5858.2648 | 2957.1453 | 1971.7076
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 109.4188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446
02 Oil Combustion | 161.4795 | 0 | 0 | 0 | 0 | 0 | 1.0584 | 1.5635 | 17.2323
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 547.0566 | 0 | 1027.9476 | 3075.4171 | 3075.417 | 3075.417 | 3075.417 | 3028.7283 | 2883.3039
03 Hydro | 5073.9838 | 5073.9825 | 5474.3845 | 5474.3841 | 5740.1774 | 5740.1773 | 5176.8618 | 4519.6595 | 4519.6604
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 253.164 | 253.164 | 253.164 | 253.164 | 253.164
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 1670.8386 | 6392.6012 | 6392.6012
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 67.5263 | 67.5263 | 210.7224 | 497.1146 | 1539.5575 | 2197.2967 | 3889.2561
06 Solar PV | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 2.7132
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773.178
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 312.4465 | 446.76 | 446.76 | 446.76
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8432 | 15167.4253 | 14956.3348 | 14827.1547 | 16428.9907 | 17833.0796 | 19856.2028 | 22331.8093 | 24762.4357
(**) Ind. Boiler generation in BBtu, not included in the total
12a. Generation by Fuel Type [GWh]
Biomass | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 313.1911 | 447.5046 | 447.5046 | 447.5046
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 4679.161 | 9953.6795 | 9386.9503 | 9093.2707 | 9857.8008 | 9962.4411 | 9233.1529 | 6285.3448 | 1971.7076
Oil | 4138.2248 | 112.2896 | 0 | 0 | 0 | 0 | 1.0584 | 1.5635 | 4304.7047
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 26.7291 | 26.7291 | 94.2553 | 94.2553 | 237.4514 | 523.8436 | 1566.2866 | 2224.0258 | 4665.1473
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 1670.8386 | 6392.6012 | 6392.6012
Water | 5073.9838 | 5073.9825 | 5474.3845 | 5474.3841 | 5993.3414 | 5993.3413 | 5430.0258 | 4772.8235 | 4772.8244
Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8432 | 15167.4253 | 14956.3348 | 14827.1547 | 16428.9907 | 17833.0796 | 19856.2028 | 22331.8093 | 24762.4357
13. Generation by Capacity Reporting Type [TBtu]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 1.0218 | 1.0218 | 1.0218 | 4.791
01 Oil/Gas Combined Cycle | 27.2941 | 34.3451 | 28.5209 | 20.5329 | 23.1415 | 22.4767 | 19.9884 | 10.0898 | 6.7275
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0.37334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406
02 Oil Combustion | 0.55097 | 0 | 0 | 0 | 0 | 0 | 0.0036113 | 0.0053346 | 0.058797
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 1.8666 | 0 | 3.5074 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.334 | 9.8378
03 Hydro | 17.3124 | 17.3124 | 18.6786 | 18.6786 | 19.5855 | 19.5855 | 17.6635 | 15.4211 | 15.4211
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 0.8638 | 0.8638 | 0.8638 | 0.8638 | 0.8638
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 5.7009 | 21.8116 | 21.8116
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 0.2304 | 0.2304 | 0.71898 | 1.6962 | 5.253 | 7.4972 | 13.2701
06 Solar PV | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0092574
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6381
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 1.0661 | 1.5243 | 1.5243 | 1.5243
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 0.56127 | 1.1589 | 3.5494 | 5.143 | 7.5335 | 7.5335
Total | 47.4911 | 51.7513 | 51.031 | 50.5903 | 56.0557 | 60.8465 | 67.7494 | 76.1961 | 84.4894
(**) Ind. Boiler generation, not included in the total
14. Capacity Factor by Capacity Reporting Type [%]
01 Potential Build Oil/Gas Combined Cycle | N/A | N/A | N/A | N/A | N/A | 89.9999 | 89.9999 | 89.9999 | 89.9999
01 Oil/Gas Combined Cycle | 61.2049 | 53.1983 | 40.6053 | 29.2327 | 32.9466 | 39.5791 | 35.1975 | 17.767 | 11.8464
02 Potential Build Biogas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Gas Combustion Turbine | 2.7452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
02 Oil Combustion | 8.3411 | 0 | 0 | 0 | 0 | 0 | 0.064097 | 0.20167 | 2.2228
02 Potential Build Oil/Gas Combustion | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Oil/Gas Combustion | 15.8116 | 0 | 15.1912 | 45.449 | 46.9666 | 46.9666 | 46.9666 | 46.2535 | 44.0327
03 Hydro | 42.279 | 42.279 | 45.6153 | 45.6153 | 47.83 | 47.83 | 43.1362 | 37.6601 | 37.6601
03 Potential Build Hydro Small | N/A | N/A | N/A | N/A | 36.125 | 36.125 | 36.125 | 36.125 | 36.125
04 Potential Build Nuclear | N/A | N/A | N/A | N/A | N/A | N/A | 95.0003 | 95 | 95
05 Potential Build Interruptible | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
06 Potential Build Solar PV | N/A | N/A | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 15.4551 | 15.5107 | 15.3777
06 Solar PV | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 17.2069
06 Potential Build Solar PV with storage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 14.4692
07 Potential Build Biomass Combustion | N/A | N/A | N/A | N/A | N/A | 59.4457 | 85 | 85 | 85
07 Potential Build Coal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
08 Potential Build Wind | N/A | N/A | N/A | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594
Average | 38.9232 | 35.4547 | 32.3028 | 31.6026 | 34.0775 | 36.0214 | 33.1278 | 31.5131 | 28.0106
(**) Ind. Boilers not included in the average
15. Total Annual Production Cost [Million US2016$](*)
Variable O&M | 42.6822 | 47.29 | 45.5467 | 43.8024 | 47.9681 | 48.4788 | 49.5387 | 47.2832 | 44.6063
Fixed O&M | 103.6056 | 148.842 | 161.93 | 165.2202 | 171.1526 | 118.4727 | 167.484 | 249.0504 | 299.8822
Fuel | 600.6945 | 637.4378 | 599.0664 | 573.0697 | 591.2262 | 630.2547 | 621.3996 | 497.6035 | 821.5208
Capital | 840.4565 | 1382.8945 | 6.3305 | 20.6095 | 102.8405 | 220.1001 | 480.1179 | 971.2254 | 1208.8078
Pollutant Transport & Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1587.4388 | 2216.4642 | 812.8737 | 802.7018 | 913.1873 | 1017.3064 | 1318.5402 | 1765.1625 | 2374.8171
Sales Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(*) Costs include only those items that are important for determining incremental cost of pollution control (industrial boiler costs are included)
15c Annual Transmission Activity (*)
[GWh] Transmitted Out Existing Lines | 7466.6884 | 9211.7869 | 9246.6999 | 9938.0826 | 11561.6713 | 11317.4112 | 16604.3971 | 16290.0477 | 16647.334
[GWh] Transmitted Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[MW] Transferred Out Existing Lines | 273 | 275 | 491.8666 | 494.8195 | 549.4105 | 640.9206 | 881.6574 | 1084.846 | 1142.062
[MW] Transferred Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Book [MW] of Transmission Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[GWh] Transmitted Out All Lines | 7466.6884 | 9211.7869 | 9246.6999 | 9938.0826 | 11561.6713 | 11317.4112 | 16604.3971 | 16290.0477 | 16647.334
[MW] Transferred Out All Lines | 273 | 275 | 491.8666 | 494.8195 | 549.4105 | 640.9206 | 881.6574 | 1084.846 | 1142.062
16. Emissions
CO2 Thousand Tons | 5387.1024 | 5183.1075 | 4705.2705 | 4509.8233 | 4898.55 | 4941.9793 | 4571.8827 | 3080.2804 | 3556.311
NOX Thousand Tons | 23.5331 | 40.1214 | 36.9041 | 35.3712 | 38.42 | 37.9274 | 35.018 | 23.3161 | 7.8237
SO2 Thousand Tons | 10.1178 | 1.1401 | 0.75486 | 0.7235 | 0.78586 | 0.79283 | 0.73332 | 0.49396 | 0.16211
(**) Industrial Boiler emissions are included
17. Fuel Consumption by Fuel and Fuel Type [TBtu]
Fuel Type | 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
Biomass | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 4.2281 | 6.0413 | 6.0413 | 6.0413
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 35.8097 | 78.1225 | 72.1177 | 69.1221 | 75.0801 | 75.7458 | 70.0604 | 47.1925 | 15.2872
Oil | 34.145 | 0.95603 | 0 | 0 | 0 | 0 | 0.010506 | 0.015519 | 31.9852
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 17.2096 | 65.8438 | 65.8438
Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LowREHighCost
Back to Contents
| 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
1. Reserve Margin Capacity Annual [MW] | 3348.7611 | 4649.4823 | 4557.3801 | 5131.924 | 5112.044 | 4790.0287 | 5296.4537 | 6338.8277 | 7814.5957
Plus Firm Contract Purchases Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Transmission In Annual [MW] | 173 | 173 | 449.625 | 509.2398 | 618.9336 | 750.2462 | 1144.926 | 1491.1568 | 2285.7662
Less Firm Contract Sales Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Transmission Out Annual [MW] | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
Total Reserve Margin Capacity Annual [MW] | 3248.7611 | 4547.4823 | 4453.3401 | 5025.803 | 4998.528 | 4608.8197 | 5024.2927 | 6009.5316 | 7464.1588
2. Peak Load Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
Less DSM [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
3. Reserve Margin Annual [%] | 52.8408 | 94.0481 | 78.466 | 87.7536 | 50.7538 | 25.281 | 17.881 | 15 | 15
3a.Local Reserves Annual [%] | 157.5454 | 198.4006 | 182.6353 | 191.7181 | 154.1774 | 130.2068 | 124.2665 | 121.3015 | 120.3992
4. Total Generation [GWh] | 13918.8425 | 15531.5309 | 17387.3071 | 17998.0364 | 23370.6908 | 26198.5191 | 30668.0044 | 37352.4711 | 45790.2881
Inter-Region Transmission [GWh] | 378.6318 | 370.9516 | -441.5621 | 355.1277 | -278.1665 | -718.4011 | -1320.2731 | -1622.8298 | -1679.9118
Pumping & Storage Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Purchases [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Sales [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Total Supply for Demand [GWh] | 14297.4742 | 15902.4825 | 16945.745 | 18353.1641 | 23092.5243 | 25480.118 | 29347.7313 | 35729.6413 | 44110.3763
6. Projected Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
Energy Not Served [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less DSM [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Demand Response [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
7. Dumped Energy [GWh] | -0.0015163 | -0.0018965 | 0.0015398 | 0.001506 | -0.00090984 | 0.00016806 | 0.004482 | -0.019057 | 0.028838
8. Total Generation [GWh] | 13918.8425 | 15531.5309 | 17387.3071 | 17998.0364 | 23370.6908 | 26198.5191 | 30668.0044 | 37352.4711 | 45790.2881
Less T&D Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9. Total Sales [GWh] | 13918.8425 | 15531.5309 | 17387.3071 | 17998.0364 | 23370.6908 | 26198.5191 | 30668.0044 | 37352.4711 | 45790.2881
10. Capacity by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 524.4097 | 1636.7837 | 3112.5517
01 Oil/Gas Combined Cycle | 1492 | 2160 | 2350 | 2350 | 2350 | 1900 | 1900 | 1900 | 1900
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 455 | 504.92 | 504.92 | 504.92 | 455 | 455 | 455 | 455 | 455
02 MSW - Landfill Gas | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
02 Oil Combustion | 221 | 221 | 221 | 221 | 188.5 | 188.5 | 188.5 | 88.5 | 88.5
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 394.96 | 394.96 | 772.46 | 772.46 | 747.5 | 747.5 | 747.5 | 747.5 | 747.5
03 Hydro | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 80 | 80
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 47.1565 | 147.1565 | 347.1565 | 597.1565 | 1077.1565 | 2347.1565
06 Solar PV | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 1.8
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 145.4386 | 445.4386 | 645.4386 | 945.4386 | 945.4386
Total | 4082.161 | 4887.882 | 5285.4365 | 5355.8751 | 5503.4951 | 5651.4798 | 6587.9048 | 8380.2788 | 11108.0468
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
11. Capacity Additions and Changes by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 486.425 | 1112.374 | 1475.768
01 Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 0 | 100 | 200 | 250 | 480 | 1270
06 Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 75 | 300 | 200 | 300 | 0
Total | 129.301 | 217.102 | 47.1565 | 70.4386 | 255 | 597.9847 | 936.425 | 1892.374 | 2745.768
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
12. Generation by Capacity Reporting Type [GWh]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 299.4711 | 4134.4489 | 12904.3845 | 24539.388
01 Oil/Gas Combined Cycle | 7999.4308 | 10430.0748 | 8969.4982 | 9188.7352 | 13444.703 | 14438.1544 | 14199.0832 | 10900.3513 | 6038.8617
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 366.0333 | 0 | 1813.32 | 0 | 0 | 101.1435 | 149.6574 | 4.5712 | 0.93205
02 MSW - Landfill Gas | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446
02 Oil Combustion | 161.4795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 290.4422 | 0 | 1035.1044 | 3075.417 | 3075.417 | 3075.417 | 3075.417 | 3075.417 | 3075.417
03 Hydro | 5073.9831 | 5073.9825 | 5474.3846 | 5474.3843 | 5974.8822 | 5974.8824 | 5974.8836 | 5974.8835 | 5974.8823
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 297.84 | 297.84 | 297.84 | 297.84 | 297.84
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 67.5263 | 67.5263 | 210.7224 | 497.1146 | 855.1048 | 1512.844 | 3204.8034
06 Solar PV | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 2.7132
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 446.76 | 446.76 | 446.76 | 446.76
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8425 | 15531.5309 | 17387.3071 | 17998.0364 | 23370.6908 | 26198.5191 | 30668.0044 | 37352.4711 | 45790.2881
(**) Ind. Boiler generation in BBtu, not included in the total
12a. Generation by Fuel Type [GWh]
Biomass | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 447.5046 | 447.5046 | 447.5046 | 447.5046
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 4938.2835 | 10430.0748 | 11817.9226 | 12264.1522 | 16520.12 | 17914.186 | 21558.6065 | 26884.7241 | 33654.5987
Oil | 3879.1022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 26.7291 | 26.7291 | 94.2553 | 94.2553 | 237.4514 | 523.8436 | 881.8339 | 1539.5731 | 3207.5166
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 5073.9831 | 5073.9825 | 5474.3846 | 5474.3843 | 6272.7222 | 6272.7224 | 6272.7236 | 6272.7235 | 6272.7223
Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8425 | 15531.5309 | 17387.3071 | 17998.0364 | 23370.6908 | 26198.5191 | 30668.0044 | 37352.4711 | 45790.2881
13. Generation by Capacity Reporting Type [TBtu]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 1.0218 | 14.1067 | 44.0298 | 83.7284
01 Oil/Gas Combined Cycle | 27.2941 | 35.5874 | 30.6039 | 31.352 | 45.8733 | 49.263 | 48.4473 | 37.192 | 20.6046
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 1.2489 | 0 | 6.187 | 0 | 0 | 0.3451 | 0.51063 | 0.015597 | 0.0031802
02 MSW - Landfill Gas | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406
02 Oil Combustion | 0.55097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0.99099 | 0 | 3.5318 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933
03 Hydro | 17.3124 | 17.3124 | 18.6786 | 18.6786 | 20.3863 | 20.3863 | 20.3863 | 20.3863 | 20.3863
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 1.0162
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 0.2304 | 0.2304 | 0.71898 | 1.6962 | 2.9176 | 5.1618 | 10.9348
06 Solar PV | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0092574
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 1.5243 | 1.5243 | 1.5243 | 1.5243
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 0.56127 | 1.1589 | 3.5494 | 5.143 | 7.5335 | 7.5335
Total | 47.4911 | 52.9936 | 59.3255 | 61.4093 | 79.7408 | 89.3893 | 104.6392 | 127.4466 | 156.2365
(**) Ind. Boiler generation, not included in the total
14. Capacity Factor by Capacity Reporting Type [%]
01 Potential Build Oil/Gas Combined Cycle | N/A | N/A | N/A | N/A | N/A | 89.9999 | 90.0001 | 89.9999 | 90.0001
01 Oil/Gas Combined Cycle | 61.2049 | 55.1226 | 43.5709 | 44.6358 | 65.3099 | 86.7469 | 85.3105 | 65.4912 | 36.2825
02 Potential Build Biogas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Gas Combustion Turbine | 9.1834 | 0 | 40.9966 | 0 | 0 | 2.5376 | 3.7548 | 0.11469 | 0.023384
02 MSW - Landfill Gas | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
02 Oil Combustion | 8.3411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Oil/Gas Combustion | 8.3946 | 0 | 15.2969 | 45.449 | 46.9666 | 46.9666 | 46.9666 | 46.9666 | 46.9666
03 Hydro | 42.279 | 42.279 | 45.6153 | 45.6153 | 49.7857 | 49.7857 | 49.7857 | 49.7857 | 49.7857
03 Potential Build Hydro Small | N/A | N/A | N/A | N/A | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
04 Potential Build Nuclear | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
05 Potential Build Interruptible | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
06 Potential Build Solar PV | N/A | N/A | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.0329 | 15.5867
06 Solar PV | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 17.2069
06 Potential Build Solar PV with storage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
07 Potential Build Biomass Combustion | N/A | N/A | N/A | N/A | N/A | 85 | 85 | 85 | 85
07 Potential Build Coal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
08 Potential Build Wind | N/A | N/A | N/A | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594
Average | 38.9232 | 36.2735 | 37.5532 | 38.3611 | 48.4762 | 52.9189 | 53.1415 | 50.8811 | 47.0578
(**) Ind. Boilers not included in the average
15. Total Annual Production Cost [Million US2016$](*)
Variable O&M | 42.9388 | 48.5644 | 53.0709 | 56.0715 | 73.7065 | 80.6913 | 93.4186 | 110.0705 | 127.7045
Fixed O&M | 103.6056 | 148.842 | 161.93 | 165.2202 | 171.1526 | 118.4727 | 141.3111 | 182.8247 | 236.6112
Fuel | 586.7731 | 661.392 | 831.0153 | 799.3597 | 1188.8239 | 1515.2341 | 1964.1935 | 2774.9127 | 3998.7546
Capital | 840.4565 | 1411.163 | 6.3305 | 13.7096 | 67.0012 | 139.1056 | 233.2647 | 419.092 | 668.3792
Pollutant Transport & Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1573.774 | 2269.9614 | 1052.3468 | 1034.3611 | 1500.6842 | 1853.5037 | 2432.1879 | 3486.8999 | 5031.4495
Sales Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(*) Costs include only those items that are important for determining incremental cost of pollution control (industrial boiler costs are included)
15c Annual Transmission Activity (*)
[GWh] Transmitted Out Existing Lines | 5604.8509 | 9856.3496 | 8106.2166 | 11237.9206 | 13364.7496 | 19808.6853 | 22888.4265 | 18904.0565 | 22083.7061
[GWh] Transmitted Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[MW] Transferred Out Existing Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
[MW] Transferred Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Book [MW] of Transmission Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[GWh] Transmitted Out All Lines | 5604.8509 | 9856.3496 | 8106.2166 | 11237.9206 | 13364.7496 | 19808.6853 | 22888.4265 | 18904.0565 | 22083.7061
[MW] Transferred Out All Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
16. Emissions
CO2 Thousand Tons | 5292.477 | 5384.3682 | 6516.942 | 6280.8793 | 8405.9747 | 9160.1447 | 10871.1288 | 13134.9743 | 16185.9446
NOX Thousand Tons | 24.4837 | 42.2303 | 51.1133 | 49.2618 | 65.9292 | 71.011 | 73.7597 | 67.1132 | 58.6683
SO2 Thousand Tons | 9.5141 | 0.8638 | 1.0455 | 1.0076 | 1.3486 | 1.4695 | 1.744 | 2.1072 | 2.5967
(**) Industrial Boiler emissions are included
17. Fuel Consumption by Fuel and Fuel Type [TBtu]
Fuel Type | 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
Biomass | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 6.0413 | 6.0413 | 6.0413 | 6.0413
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 38.2185 | 82.5263 | 99.8852 | 96.2671 | 128.8385 | 140.3976 | 166.6219 | 201.3199 | 248.0821
Oil | 31.3479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## LowConCapCost
Back to Contents
| 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
1. Reserve Margin Capacity Annual [MW] | 3348.7611 | 4649.4823 | 4557.3801 | 5131.924 | 5112.044 | 4790.0287 | 5296.4537 | 6338.8277 | 7814.5957
Plus Firm Contract Purchases Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Transmission In Annual [MW] | 173 | 173 | 449.625 | 509.2398 | 618.9336 | 750.2462 | 1144.926 | 1491.1568 | 2285.7662
Less Firm Contract Sales Annual [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Transmission Out Annual [MW] | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
Total Reserve Margin Capacity Annual [MW] | 3248.7611 | 4547.4823 | 4453.3401 | 5025.803 | 4998.528 | 4608.8197 | 5024.2927 | 6009.5316 | 7464.1588
2. Peak Load Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
Less DSM [MW] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand Annual [MW] | 2125.5848 | 2343.4823 | 2495.3444 | 2676.8074 | 3315.6893 | 3678.7853 | 4262.1748 | 5225.6801 | 6490.573
3. Reserve Margin Annual [%] | 52.8408 | 94.0481 | 78.466 | 87.7536 | 50.7538 | 25.281 | 17.881 | 15 | 15
3a.Local Reserves Annual [%] | 157.5454 | 198.4006 | 182.6353 | 191.7181 | 154.1774 | 130.2068 | 124.2665 | 121.3015 | 120.3992
4. Total Generation [GWh] | 13918.8448 | 15531.532 | 17387.3049 | 17998.0357 | 23370.6928 | 26198.5195 | 30668.0033 | 37352.4731 | 45790.2897
Inter-Region Transmission [GWh] | 378.6315 | 370.9514 | -441.5621 | 355.1276 | -278.1663 | -718.4014 | -1320.273 | -1622.8296 | -1679.9117
Pumping & Storage Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plus Purchases [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less Sales [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Total Supply for Demand [GWh] | 14297.4763 | 15902.4834 | 16945.7428 | 18353.1634 | 23092.5264 | 25480.1182 | 29347.7303 | 35729.6435 | 44110.378
6. Projected Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
Energy Not Served [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Less DSM [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Demand Response [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Demand [GWh] | 14297.4757 | 15902.4844 | 16945.7435 | 18353.1626 | 23092.5252 | 25480.1178 | 29347.7268 | 35729.6604 | 44110.3475
7. Dumped Energy [GWh] | 0.00055471 | -0.0010328 | -0.00068287 | 0.00082075 | 0.0012067 | 0.0003516 | 0.0034805 | -0.016869 | 0.030497
8. Total Generation [GWh] | 13918.8448 | 15531.532 | 17387.3049 | 17998.0357 | 23370.6928 | 26198.5195 | 30668.0033 | 37352.4731 | 45790.2897
Less T&D Losses [GWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9. Total Sales [GWh] | 13918.8448 | 15531.532 | 17387.3049 | 17998.0357 | 23370.6928 | 26198.5195 | 30668.0033 | 37352.4731 | 45790.2897
10. Capacity by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 524.4097 | 1636.7837 | 3112.5517
01 Oil/Gas Combined Cycle | 1492 | 2160 | 2350 | 2350 | 2350 | 1900 | 1900 | 1900 | 1900
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 455 | 504.92 | 504.92 | 504.92 | 455 | 455 | 455 | 455 | 455
02 MSW - Landfill Gas | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
02 Oil Combustion | 221 | 221 | 221 | 221 | 188.5 | 188.5 | 188.5 | 88.5 | 88.5
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 394.96 | 394.96 | 772.46 | 772.46 | 747.5 | 747.5 | 747.5 | 747.5 | 747.5
03 Hydro | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 80 | 80 | 80 | 80
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 47.1565 | 147.1565 | 347.1565 | 597.1565 | 1077.1565 | 2347.1565
06 Solar PV | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 1.8
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 60
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 145.4386 | 445.4386 | 645.4386 | 945.4386 | 945.4386
Total | 4082.161 | 4887.882 | 5285.4365 | 5355.8751 | 5503.4951 | 5651.4798 | 6587.9048 | 8380.2788 | 11108.0468
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
11. Capacity Additions and Changes by Capacity Reporting Type [MW]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 37.9847 | 486.425 | 1112.374 | 1475.768
01 Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 MSW - Landfill Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 129.301 | 217.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 47.1565 | 0 | 100 | 200 | 250 | 480 | 1270
06 Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 70.4386 | 75 | 300 | 200 | 300 | 0
Total | 129.301 | 217.102 | 47.1565 | 70.4386 | 255 | 597.9847 | 936.425 | 1892.374 | 2745.768
(**) Ind. Boiler capacity in MMBtu/hr, not included in the total
12. Generation by Capacity Reporting Type [GWh]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 299.4711 | 4134.4489 | 12904.386 | 24539.388
01 Oil/Gas Combined Cycle | 7999.4325 | 10430.0762 | 8871.6578 | 9188.736 | 13444.7039 | 14438.1543 | 14199.0829 | 10900.3513 | 6038.8625
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 366.0332 | 0 | 1813.32 | 0 | 0 | 101.1435 | 149.6574 | 4.5712 | 0.93205
02 MSW - Landfill Gas | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446
02 Oil Combustion | 161.4795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 290.4418 | 0 | 1132.9439 | 3075.4169 | 3075.4171 | 3075.417 | 3075.4168 | 3075.417 | 3075.417
03 Hydro | 5073.9841 | 5073.9821 | 5474.3833 | 5474.383 | 5974.8833 | 5974.8829 | 5974.8831 | 5974.8839 | 5974.8831
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 297.84 | 297.84 | 297.84 | 297.84 | 297.84
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 67.5263 | 67.5263 | 210.7224 | 497.1146 | 855.1048 | 1512.844 | 3204.8034
06 Solar PV | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 26.7291 | 2.7132
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 446.76 | 446.76 | 446.76 | 446.76
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8448 | 15531.532 | 17387.3049 | 17998.0357 | 23370.6928 | 26198.5195 | 30668.0033 | 37352.4731 | 45790.2897
(**) Ind. Boiler generation in BBtu, not included in the total
12a. Generation by Fuel Type [GWh]
Biomass | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 0.7446 | 447.5046 | 447.5046 | 447.5046 | 447.5046
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 4936.3941 | 10430.0762 | 11817.9217 | 12264.1529 | 16520.121 | 17914.1859 | 21558.6059 | 26884.7255 | 33654.5995
Oil | 3880.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 26.7291 | 26.7291 | 94.2553 | 94.2553 | 237.4514 | 523.8436 | 881.8339 | 1539.5731 | 3207.5166
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 5073.9841 | 5073.9821 | 5474.3833 | 5474.383 | 6272.7233 | 6272.7229 | 6272.7231 | 6272.7239 | 6272.7231
Wind | 0 | 0 | 0 | 164.5 | 339.6525 | 1040.2625 | 1507.3359 | 2207.9459 | 2207.9459
Total | 13918.8448 | 15531.532 | 17387.3049 | 17998.0357 | 23370.6928 | 26198.5195 | 30668.0033 | 37352.4731 | 45790.2897
13. Generation by Capacity Reporting Type [TBtu]
01 Potential Build Oil/Gas Combined Cycle | 0 | 0 | 0 | 0 | 0 | 1.0218 | 14.1067 | 44.0298 | 83.7284
01 Oil/Gas Combined Cycle | 27.2941 | 35.5874 | 30.2701 | 31.352 | 45.8733 | 49.263 | 48.4473 | 37.192 | 20.6046
02 Potential Build Biogas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Gas Combustion Turbine | 1.2489 | 0 | 6.187 | 0 | 0 | 0.3451 | 0.51063 | 0.015597 | 0.0031802
02 MSW - Landfill Gas | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406 | 0.0025406
02 Oil Combustion | 0.55097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Oil/Gas Combustion | 0.99099 | 0 | 3.8656 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933 | 10.4933
03 Hydro | 17.3124 | 17.3124 | 18.6786 | 18.6786 | 20.3863 | 20.3863 | 20.3863 | 20.3863 | 20.3863
03 Potential Build Hydro Small | 0 | 0 | 0 | 0 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 1.0162
04 Potential Build Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05 Potential Build Interruptible | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06 Potential Build Solar PV | 0 | 0 | 0.2304 | 0.2304 | 0.71898 | 1.6962 | 2.9176 | 5.1618 | 10.9348
06 Solar PV | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0912 | 0.0092574
06 Potential Build Solar PV with storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
07 Potential Build Biomass Combustion | 0 | 0 | 0 | 0 | 0 | 1.5243 | 1.5243 | 1.5243 | 1.5243
07 Potential Build Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
08 Potential Build Wind | 0 | 0 | 0 | 0.56127 | 1.1589 | 3.5494 | 5.143 | 7.5335 | 7.5335
Total | 47.4911 | 52.9936 | 59.3255 | 61.4093 | 79.7408 | 89.3893 | 104.6392 | 127.4466 | 156.2365
(**) Ind. Boiler generation, not included in the total
14. Capacity Factor by Capacity Reporting Type [%]
01 Potential Build Oil/Gas Combined Cycle | N/A | N/A | N/A | N/A | N/A | 89.9999 | 90.0001 | 89.9999 | 90.0001
01 Oil/Gas Combined Cycle | 61.2049 | 55.1226 | 43.0956 | 44.6358 | 65.3099 | 86.7469 | 85.3105 | 65.4912 | 36.2825
02 Potential Build Biogas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Gas Combustion Turbine | 9.1834 | 0 | 40.9966 | 0 | 0 | 2.5376 | 3.7548 | 0.11469 | 0.023384
02 MSW - Landfill Gas | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
02 Oil Combustion | 8.3411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
02 Potential Build Oil/Gas Combustion | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
02 Oil/Gas Combustion | 8.3946 | 0 | 16.7428 | 45.449 | 46.9666 | 46.9666 | 46.9666 | 46.9666 | 46.9666
03 Hydro | 42.279 | 42.279 | 45.6153 | 45.6153 | 49.7857 | 49.7857 | 49.7857 | 49.7857 | 49.7857
03 Potential Build Hydro Small | N/A | N/A | N/A | N/A | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
04 Potential Build Nuclear | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
05 Potential Build Interruptible | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
06 Potential Build Solar PV | N/A | N/A | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.3466 | 16.0329 | 15.5867
06 Solar PV | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 15.4104 | 17.2069
06 Potential Build Solar PV with storage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
07 Potential Build Biomass Combustion | N/A | N/A | N/A | N/A | N/A | 85 | 85 | 85 | 85
07 Potential Build Coal | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
08 Potential Build Wind | N/A | N/A | N/A | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594 | 26.6594
Average | 38.9232 | 36.2735 | 37.5532 | 38.3611 | 48.4762 | 52.9189 | 53.1415 | 50.8811 | 47.0578
(**) Ind. Boilers not included in the average
15. Total Annual Production Cost [Million US2016$](*)
Variable O&M | 42.9388 | 48.5644 | 53.0709 | 56.0715 | 73.7065 | 80.6913 | 93.4186 | 110.0705 | 127.6875
Fixed O&M | 103.6056 | 148.842 | 161.93 | 165.2202 | 171.1526 | 118.4727 | 141.3111 | 182.8247 | 236.6112
Fuel | 586.7732 | 661.3921 | 831.0153 | 799.3597 | 1086.8288 | 1293.4166 | 1578.0739 | 2070.6597 | 2798.3247
Capital | 840.4565 | 1411.163 | 6.3305 | 18.0991 | 86.3254 | 183.6105 | 272.8839 | 436.1468 | 643.3498
Pollutant Transport & Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 1573.7741 | 2269.9615 | 1052.3467 | 1038.7506 | 1418.0132 | 1676.1911 | 2085.6875 | 2799.7017 | 3805.9733
Sales Revenue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(*) Costs include only those items that are important for determining incremental cost of pollution control (industrial boiler costs are included)
15c Annual Transmission Activity (*)
[GWh] Transmitted Out Existing Lines | 6206.9337 | 10113.9637 | 7332.8029 | 10671.9665 | 14483.6938 | 20009.1174 | 20083.7367 | 18603.4707 | 22382.0655
[GWh] Transmitted Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[MW] Transferred Out Existing Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
[MW] Transferred Out New Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Book [MW] of Transmission Builds | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[GWh] Transmitted Out All Lines | 6206.9337 | 10113.9637 | 7332.8029 | 10671.9665 | 14483.6938 | 20009.1174 | 20083.7367 | 18603.4707 | 22382.0655
[MW] Transferred Out All Lines | 273 | 275 | 553.665 | 615.3608 | 732.4496 | 931.4552 | 1417.087 | 1820.4529 | 2636.2031
16. Emissions
CO2 Thousand Tons | 5292.4776 | 5384.369 | 6516.9415 | 6280.8797 | 8405.9752 | 9160.1447 | 10871.1285 | 13134.975 | 16186.7826
NOX Thousand Tons | 24.4837 | 42.2303 | 51.1133 | 49.2618 | 65.9292 | 71.011 | 73.7597 | 67.1132 | 58.6749
SO2 Thousand Tons | 9.5141 | 0.8638 | 1.0455 | 1.0076 | 1.3486 | 1.4695 | 1.744 | 2.1072 | 2.5968
(**) Industrial Boiler emissions are included
17. Fuel Consumption by Fuel and Fuel Type [TBtu]
Fuel Type | 2017 | 2018 | 2019 | 2020 | 2023 | 2026 | 2030 | 2035 | 2040
Biomass | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 6.0413 | 6.0413 | 6.0413 | 6.0413
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 38.2185 | 82.5263 | 99.8852 | 96.2671 | 128.8385 | 140.3976 | 166.6219 | 201.3199 | 248.095
Oil | 31.3479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uranium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0